## ASSETS
asset_code | name | min | max | parent | use_as_parent_index | use_as_sub_index
SIT | Site | 1 | 0 |  | 0 | 0
AMB | Ambient | 1 | 1 | SIT | 0 | 0
UNT | Unit | 1 | 20 | SIT | 1 | 0
OL1 | Others Level 1 | 1 | 1 | UNT | 0 | 0
STE | Steam Turbine | 1 | 0 | UNT | 0 | 0
BPV | Bypass Valve | 1 | 1 | UNT | 0 | 0
MSD | Main Steam Duct | 1 | 1 | UNT | 0 | 0
VAS | Vacuum System | 1 | 1 | UNT | 0 | 0
COS | Condensate System | 1 | 1 | UNT | 0 | 0
ACC | Air Cooled Condenser | 1 | 2 | UNT | 1 | 0
DPT | Drain Pot | 1 | 1 | MSD | 0 | 0
DPP | Drain Pump | 1 | 1 | MSD | 0 | 0
IV2 | Isolation Valve Level 2 | 0 | 1 | MSD | 0 | 0
FLT | Flash Tank | 0 | 1 | MSD | 0 | 0
COP | Condensate Pump | 2 | 5 | COS | 0 | 0
TNK | Tank | 1 | 1 | COS | 0 | 0
ACO | Adiabatic Cooling | 1 | 1 | ACC | 0 | 0
CLS | Cleaning System | 1 | 1 | ACC | 0 | 0
OL2 | Others Level 2 | 1 | 1 | ACC | 0 | 0
STR | Street | 1 | 20 | ACC | 0 | 1
CON | Condensate Line | 1 | 0 | STR | 0 | 0
ATL | Air Take-off Line | 1 | 1 | STR | 0 | 0
IV3 | Isolation Valve Level 3 | 0 | 2 | STR | 0 | 0
MOD | Module | 1 | 20 | STR | 0 | 1
OL3 | Others Level 3 | 1 | 1 | MOD | 0 | 0
FAN | Fan | 1 | 4 | MOD | 0 | 0
TRA | Transmission | 1 | 0 | MOD | 0 | 0
MOT | Motor | 1 | 0 | MOD | 0 | 0
AMP | Amplivibe | 1 | 20 | AMP | 0 | 0

## EQUIPMENTS
equipment_code | equipment_name | asset_code
STE | Steam Turbine | STE
MOT | Motor | MOT
DPT | Drain Pot | DPT
BPV | ByPassValve | DPT
IVT | Isolation valve Turbine | IV2
IVS | Isolation valve Street | IV3
SEC | Secondary | ATL
CON | Condensate line | CON
MGE | GearBox | TRA
CDT | Condensate Tank | TNK
AMB | Ambient | AMB
ACT | ACC Air Temperature | ACC
GTI | Gas Turbine Inlet | OL1
MUL | Make-up | OL3
PPA | PowerPlant | UNT
QAT | Quick Air Takeoff | ATL
HDP | Holding Pump | VAS
HGE | Hogging Ejector | VAS
PCO | Peak Cooler | ACO
ATO | Air Takeoff | ATL
AMP | Amplivibe | AMP

## LOCATIONS
loc_code | loc_name | active
BE-PSG | Engie Saint-Ghislain (BE) | Y
ACC_Demo | Customer Brussels | Y
ACC_Snap | Customer Snap | Y

## LOC_DATASHEET
LOC_CODE | Parameter | Value
BE-PSG | ACC Type | Single Row - A-Frame - Forced Draft
BE-PSG | Manufacturer | SPG Dry Cooling
BE-PSG | Number of Modules | 24
BE-PSG | Arrangement | 4 x 6
BE-PSG | Design Heat Load | 214.8 MWth
BE-PSG | Design Steam Flow | 95.42 kg/s
BE-PSG | Design Steam Backpressure | 58 mbara
BE-PSG | Design Steam Enthalpy | 2399 kJ/kg
BE-PSG | Design Steam Dryness | 0.9308 -
BE-PSG | Atmospheric Pressure | 1013 mbara
BE-PSG | Design Inlet Temperature | 10 °C
BE-PSG | Min/Max Ambient Temperature | -19 / 40 °C
BE-PSG | Design Wind Speed | 3 m/s
BE-PSG | Design Total Fan Power Cons | 1827 kWe
BE-PSG | Fan Motor Rating | 90 kW
BE-PSG | Fan Motor Control | Single speed with soft starter

## LOC_PARAMETERS
LOC_CODE | parameter_name | parameter_value | parameter_description
BE-PSG | Power_cutoff | 1.0000000000000001E-5 | Cut-off value to indicate if fan is on/off
BE-PSG | nr_street | 4 | Number of streets
BE-PSG | nr_modules_street | 6 | Number of modules in 1 street
BE-PSG | Plant_on | 120 | Cut-off for variable PPA_01_W_X_1_MW to indicate if plant is on/off
BE-PSG | Bypass_cutoff |  | Cut-off value to indicate bypass valves open/closed
BE-PSG | p1_design | 5.8000000000000003E-2 | pressure in design point
BE-PSG | x1_design | .9308 | Steam quality in design point
BE-PSG | h1_design | 2399 | h in desgin point
BE-PSG | nsi | .8281 | isentropic efficiency
BE-PSG | cosPhi | .83
BE-PSG | fan_G | 1825.7 | guaranteed fan motor power
BE-PSG | Atm_press_G | 1013 | guaranteed atmospheric presssure
BE-PSG | M_AG | 95.42 | guaranteed steam flow
BE-PSG | outlet_temp_G | 28.6 | guaranteed outlet air temp
BE-PSG | inlet_temp_G | 10 | guaranteed Inlet air temp
BE-PSG | ha_G | 2399 | guaranteed steam enthalpy
BE-PSG | Wind_speed_G | 3 | guaranteed wind speed
BE-PSG | mk | .45 | parameter to calculate capabililty
BE-PSG | n | .33 | parameter to calculate capabililty
BE-PSG | LMTD | 10.6 | parameter to calculate capabililty
BE-PSG | nr_bypass | 1 | number of bypass valves
BE-PSG | customer_name | Engie | dashboard customer name
BE-PSG | plant_name | Saint-Ghislain | dashboard site name
BE-PSG | longitude | 3.825363 | plant longitude
BE-PSG | latitude | 50.471323 | plant latitutde
BE-PSG | lb_acc_capability | 85 | lower bound threshhold acc capability (green)
BE-PSG | mb_acc_capability | 95 | medium bound threshold acc capability (orange)
BE-PSG | up_acc_capability | 120 | upper bound threshold acc capability (red)
BE-PSG | loc_cd | BE-PSG | dashboard loc cd
BE-PSG | customer_id | 1 | dashboard customer id
BE-PSG | installation_date | 01DEC1997:00:00:00 | installation date
BE-PSG | number_fans | 24 | number of total fans
BE-PSG | Plant_time_zone_info | Europe/Brussels | power plant time zone information in required SAS string format

## METADATA_ACC_NRFANS
p1_design | x1_design | h1_design | nsi | cosPhi | fan_G | Atm_press_G | M_AG | outlet_temp_G | inlet_temp_G | ha_G | Wind_speed_G | mk | n | LMTD | nr_bypass | C_0101_FAN_nr_fans_on
0.058 | 0.9308 | 2399 | 0.8281 | 0.83 | 1825.7 | 1013 | 95.42 | 28.7 | 10 | 2399 | 3 | 0.45 | 0.33 | 11.83 | 1 | 24
0.0597 | 0.9308 | 2399.3873 | 0.8281 | 0.83 | 1749.6 | 1013 | 95.42 | 29.3 | 10 | 2399.3873 | 3 | 0.45 | 0.33 | 12.13 | 1 | 23
0.0617 | 0.9308 | 2400.5245 | 0.8281 | 0.83 | 1673.6 | 1013 | 95.42 | 29.8 | 10 | 2400.5245 | 3 | 0.45 | 0.33 | 12.43 | 1 | 22
0.0638 | 0.9308 | 2401.7383 | 0.8281 | 0.83 | 1597.5 | 1013 | 95.42 | 30.5 | 10 | 2401.7383 | 3 | 0.45 | 0.33 | 12.73 | 1 | 21
0.0661 | 0.9308 | 2402.9924 | 0.8281 | 0.83 | 1521.4 | 1013 | 95.42 | 31.1 | 10 | 2402.9924 | 3 | 0.45 | 0.33 | 13.03 | 1 | 20
0.0687 | 0.9308 | 2404.3978 | 0.8281 | 0.83 | 1445.3 | 1013 | 95.42 | 31.8 | 10 | 2404.3978 | 3 | 0.45 | 0.33 | 13.43 | 1 | 19
0.0715 | 0.9308 | 2405.844 | 0.8281 | 0.83 | 1369.3 | 1013 | 95.42 | 32.5 | 10 | 2405.844 | 3 | 0.45 | 0.33 | 13.83 | 1 | 18
0.0746 | 0.9308 | 2407.4385 | 0.8281 | 0.83 | 1293.2 | 1013 | 95.42 | 33.3 | 10 | 2407.4385 | 3 | 0.45 | 0.33 | 14.23 | 1 | 17
0.0781 | 0.9308 | 2409.1189 | 0.8281 | 0.83 | 1217.1 | 1013 | 95.42 | 34.1 | 10 | 2409.1189 | 3 | 0.45 | 0.33 | 14.63 | 1 | 16
0.0821 | 0.9308 | 2410.9512 | 0.8281 | 0.83 | 1141.1 | 1013 | 95.42 | 35 | 10 | 2410.9512 | 3 | 0.45 | 0.33 | 15.13 | 1 | 15
0.0866 | 0.9308 | 2412.9364 | 0.8281 | 0.83 | 1065 | 1013 | 95.42 | 35.9 | 10 | 2412.9364 | 3 | 0.45 | 0.33 | 15.63 | 1 | 14
0.0917 | 0.9308 | 2415.0763 | 0.8281 | 0.83 | 988.9 | 1013 | 95.42 | 37 | 10 | 2415.0763 | 3 | 0.45 | 0.33 | 16.23 | 1 | 13
0.0975 | 0.9308 | 2417.4089 | 0.8281 | 0.83 | 912.9 | 1013 | 95.42 | 38.1 | 10 | 2417.4089 | 3 | 0.45 | 0.33 | 16.83 | 1 | 12
0.1043 | 0.9308 | 2419.9721 | 0.8281 | 0.83 | 836.8 | 1013 | 95.42 | 39.3 | 10 | 2419.9721 | 3 | 0.45 | 0.33 | 17.43 | 1 | 11
0.1122 | 0.9308 | 2422.7663 | 0.8281 | 0.83 | 760.7 | 1013 | 95.42 | 40.6 | 10 | 2422.7663 | 3 | 0.45 | 0.33 | 18.23 | 1 | 10
0.1215 | 0.9308 | 2425.8289 | 0.8281 | 0.83 | 684.6 | 1013 | 95.42 | 42.1 | 10 | 2425.8289 | 3 | 0.45 | 0.33 | 18.93 | 1 | 9
0.1325 | 0.9308 | 2429.235 | 0.8281 | 0.83 | 608.6 | 1013 | 95.42 | 43.7 | 10 | 2429.235 | 3 | 0.45 | 0.33 | 19.83 | 1 | 8
0.1457 | 0.9308 | 2432.9831 | 0.8281 | 0.83 | 532.5 | 1013 | 95.42 | 45.4 | 10 | 2432.9831 | 3 | 0.45 | 0.33 | 20.73 | 1 | 7
0.1619 | 0.9308 | 2437.1842 | 0.8281 | 0.83 | 456.4 | 1013 | 95.42 | 47.4 | 10 | 2437.1842 | 3 | 0.45 | 0.33 | 21.83 | 1 | 6
0.1817 | 0.9308 | 2441.8682 | 0.8281 | 0.83 | 380.4 | 1013 | 95.42 | 49.5 | 10 | 2441.8682 | 3 | 0.45 | 0.33 | 23.03 | 1 | 5
0.2066 | 0.9308 | 2447.1497 | 0.8281 | 0.83 | 304.3 | 1013 | 95.42 | 52 | 10 | 2447.1497 | 3 | 0.45 | 0.33 | 24.33 | 1 | 4
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
0.2074 | 0.9308 | 2447.3015 | 0.8281 | 0.83 | 0 | 1013 | 95.42 | 57.8 | 10 | 2447.3015 | 3 | 0.45 | 0.33 | 17.63 | 1 | 0

## LOC_WEATHERDATA
loc_code | http_request
BE-PSG | http://api.openweathermap.org/data/2.5/forecast?q=saint-ghislain,be&appid=381e87fefac8162026535db25f9f7946

## LIB_CONNECTIONS
name | dataset | content
ICARE_ENG | ICAREDB.Tag | TAG
ICARE_ENG | ICAREDB.Tag_Facts | FACT

## PI_CONNECTIONS
name | server | dataserver | username | password
PI_ENG | https://bugen.engie.com | piatlas.myengie.com | mahima.swarup@spxdrycooling.com | EM3nt9vDSNkpkaLUaiXn

## TAG_MAPPING
TAG_ID | TAG_NM | ASSET_ID | TAG_COLUMN_NM | loc_code | asset_code | generic_tag_name | tag_source | parent_id | equipment_code | sub_id | type | media | redundancy | tag_unit | source_tag_scope | source_tag_id | source_tag_unit | description | get_data | every_20min | frequency | start_dt | comment
BE-PSG_D_0101_ACT_01_T_A_1_C | D_0101_ACT_01_T_A_1_C | BE-PSG_0101_ACC | ACT_01_T_A_1_C | BE-PSG | ACC | D_0101_ACT_01_T_A_1_C | D | 0101 | ACT | 01 | T | A | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG10-CT501-X3V | C | TEMPERATURE AMBIANTE - 2/3 | Y | Y | 00:01 | 20454 | RGV10MAG50CT503_XJ51
BE-PSG_D_0101_AMB_01_H_A_1_C | D_0101_AMB_01_H_A_1_C | BE-PSG_0101_AMB | AMB_01_H_A_1_C | BE-PSG | AMB | D_0101_AMB_01_H_A_1_C | D | 0101 | AMB | 01 | H | A | 1 | C | piatlas.myengie.com | BE-PSG-01-MBL30-CM513-XC7 | C | humidité relative site | Y | Y | 00:01 | 20454 | calculated feature
BE-PSG_D_0101_AMB_01_P_A_1_Atm | D_0101_AMB_01_P_A_1_Atm | BE-PSG_0101_AMB | AMB_01_P_A_1_Atm | BE-PSG | AMB | D_0101_AMB_01_P_A_1_Atm | D | 0101 | AMB | 01 | P | A | 1 | Atm | piatlas.myengie.com | BE-PSG-01-MBA10-CP503-XC7 | mbar | Pression atmospherique site | Y | Y | 00:01 | 20454 | RGV10QUY60CP505_XQ50
BE-PSG_D_0101_AMB_01_P_A_1_kPa | D_0101_AMB_01_P_A_1_kPa | BE-PSG_0101_AMB | AMB_01_P_A_1_kPa | BE-PSG | AMB | D_0101_AMB_01_P_A_1_kPa | D | 0101 | AMB | 01 | P | A | 1 | kPa | piatlas.myengie.com | BE-PSG-01-MBA10-CP503-XC7 | mbar | Pression atmospherique site | Y | Y | 00:01 | 20454 | RGV10QUY60CP505_XQ50
BE-PSG_D_0101_AMB_01_T_A_1_C | D_0101_AMB_01_T_A_1_C | BE-PSG_0101_AMB | AMB_01_T_A_1_C | BE-PSG | AMB | D_0101_AMB_01_T_A_1_C | D | 0101 | AMB | 01 | T | A | 1 | C | piatlas.myengie.com | BE-PSG-01-HA00-CT501-X1V | C | Temperature air messure site | Y | Y | 00:01 | 20454 | RGV10MAG50CT503_XJ51
BE-PSG_D_0101_ATO_01_O_W_1_Perc | D_0101_ATO_01_O_W_1_Perc | BE-PSG_0101_ATL | ATO_01_O_W_1_Perc | BE-PSG | ATL | D_0101_ATO_01_O_W_1_Perc | D | 0101 | ATO | 01 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ11-AA100M-XS0 | Bin | VN VIDE RANGEE 1 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_ATO_04_O_W_1_Perc | D_0101_ATO_04_O_W_1_Perc | BE-PSG_0101_ATL | ATO_04_O_W_1_Perc | BE-PSG | ATL | D_0101_ATO_04_O_W_1_Perc | D | 0101 | ATO | 04 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ14-AA100M-XS0 | Bin | VN VIDE RANGEE 4 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_BPV_01_O_S_1_Perc | D_0101_BPV_01_O_S_1_Perc | BE-PSG_0101_BPV | BPV_01_O_S_1_Perc | BE-PSG | BPV | D_0101_BPV_01_O_S_1_Perc | D | 0101 | BPV | 01 | O | S | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAN10-AA100X-X6V | Perc | VANNE BY PASS BP - SORTIE CSG POS. | N | N | 00:01 | 20454 | RGV10MAN10AA201XXJ51
BE-PSG_D_0101_BPV_01_O_W_1_Perc | D_0101_BPV_01_O_W_1_Perc | BE-PSG_0101_BPV | BPV_01_O_W_1_Perc | BE-PSG | BPV | D_0101_BPV_01_O_W_1_Perc | D | 0101 | BPV | 01 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-LAE10-CG100C-X1V | Perc | POS VN REGL DESURCH CONT TV BP | Y | Y | 00:01 | 20454
BE-PSG_D_0101_BPV_01_P_S_1_bar | D_0101_BPV_01_P_S_1_bar | BE-PSG_0101_BPV | BPV_01_P_S_1_bar | BE-PSG | BPV | D_0101_BPV_01_P_S_1_bar | D | 0101 | BPV | 01 | P | S | 1 | bar | piatlas.myengie.com | BE-PSG-01-MAN10-CP501-X1V | psi | PRESSION CSG BY-P BP | N | N | 00:01 | 20454
BE-PSG_D_0101_BPV_01_T_S_1_C | D_0101_BPV_01_T_S_1_C | BE-PSG_0101_BPV | BPV_01_T_S_1_C | BE-PSG | BPV | D_0101_BPV_01_T_S_1_C | D | 0101 | BPV | 01 | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAN11-CT501A-X1V | C | TEMP VAP GAINE SORTIE BY PASS BP | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_BPV_01_T_S_2_C | D_0101_BPV_01_T_S_2_C | BE-PSG_0101_BPV | BPV_01_T_S_2_C | BE-PSG | BPV | D_0101_BPV_01_T_S_2_C | D | 0101 | BPV | 01 | T | S | 2 | C | piatlas.myengie.com | BE-PSG-01-MAN11-CT501B-X1V | C | TEMP VAP GAINE SORTIE BY PASS BP | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_BPV_02_F_W_1_ton_h | D_0101_BPV_02_F_W_1_ton_h | BE-PSG_0101_BPV | BPV_02_F_W_1_ton_h | BE-PSG | BPV | D_0101_BPV_02_F_W_1_ton_h | D | 0101 | BPV | 02 | F | W | 1 | ton_h | piatlas.myengie.com | BE-PSG-01-LAE30-CF501-X1V | ton_h | DEBIT DESURCH CONT TURBINE MP | Y | Y | 00:01 | 20454
BE-PSG_D_0101_BPV_02_O_S_1_Perc | D_0101_BPV_02_O_S_1_Perc | BE-PSG_0101_BPV | BPV_02_O_S_1_Perc | BE-PSG | BPV | D_0101_BPV_02_O_S_1_Perc | D | 0101 | BPV | 02 | O | S | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAN30-AA100X-X2H | Perc | VANNE BY PASS MP - RET. MANU POS. | Y | Y | 00:01 | 20454 | RGV10MAN20AA211_XJ51
BE-PSG_D_0101_BPV_02_O_W_1_Perc | D_0101_BPV_02_O_W_1_Perc | BE-PSG_0101_BPV | BPV_02_O_W_1_Perc | BE-PSG | BPV | D_0101_BPV_02_O_W_1_Perc | D | 0101 | BPV | 02 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-LAE30-CG100C-X1V | Perc | POS VN REGL DESURCH CONT TV MP | Y | Y | 00:01 | 20454
BE-PSG_D_0101_BPV_02_T_S_1_C | D_0101_BPV_02_T_S_1_C | BE-PSG_0101_BPV | BPV_02_T_S_1_C | BE-PSG | BPV | D_0101_BPV_02_T_S_1_C | D | 0101 | BPV | 02 | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAN31-CT501A-X1V | C | TEMP VAP GAINE SORTIE BY PASS MP | N | N | 00:01 | 20454
BE-PSG_D_0101_BPV_02_T_S_2_C | D_0101_BPV_02_T_S_2_C | BE-PSG_0101_BPV | BPV_02_T_S_2_C | BE-PSG | BPV | D_0101_BPV_02_T_S_2_C | D | 0101 | BPV | 02 | T | S | 2 | C | piatlas.myengie.com | BE-PSG-01-MAN31-CT501B-X1V | C | TEMP VAP GAINE SORTIE BY PASS MP | N | N | 00:01 | 20454
BE-PSG_D_0101_CDT_01_L_W_1_mm | D_0101_CDT_01_L_W_1_mm | BE-PSG_0101_TNK | CDT_01_L_W_1_mm | BE-PSG | TNK | D_0101_CDT_01_L_W_1_mm | D | 0101 | CDT | 01 | L | W | 1 | mm | piatlas.myengie.com | BE-PSG-01-LCB01-CL501-X31V | mm | NIVEAU BAC RECUP CONDEN -2/3 _ 1 | Y | Y | 00:01 | 20454 | RGV10MAG50CL507_XJ51
BE-PSG_D_0101_CDT_01_L_W_2_mm | D_0101_CDT_01_L_W_2_mm | BE-PSG_0101_TNK | CDT_01_L_W_2_mm | BE-PSG | TNK | D_0101_CDT_01_L_W_2_mm | D | 0101 | CDT | 01 | L | W | 2 | mm | piatlas.myengie.com | BE-PSG-01-LCB01-CL501-X32V | mm | NIVEAU BAC RECUP CONDEN -2/3 _ 2 | N | N | 00:01 | 20454 | RGV10MAG50CL507_XJ51
BE-PSG_D_0101_CDT_01_L_W_3_mm | D_0101_CDT_01_L_W_3_mm | BE-PSG_0101_TNK | CDT_01_L_W_3_mm | BE-PSG | TNK | D_0101_CDT_01_L_W_3_mm | D | 0101 | CDT | 01 | L | W | 3 | mm | piatlas.myengie.com | BE-PSG-01-LCB01-CL501-X33V | mm | NIVEAU BAC RECUP CONDEN -2/3 _ 3 | N | N | 00:01 | 20454 | RGV10MAG50CL507_XJ51
BE-PSG_D_0101_CON_01L_T_S_1_C | D_0101_CON_01L_T_S_1_C | BE-PSG_0101_CON | CON_01L_T_S_1_C | BE-PSG | CON | D_0101_CON_01L_T_S_1_C | D | 0101 | CON | 01L | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG11-CT502-X1V | C | TEMP AEROCDSR MOITIE 1ER RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ51CT502_XQ50
BE-PSG_D_0101_CON_01R_T_S_1_C | D_0101_CON_01R_T_S_1_C | BE-PSG_0101_CON | CON_01R_T_S_1_C | BE-PSG | CON | D_0101_CON_01R_T_S_1_C | D | 0101 | CON | 01R | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG11-CT501-X1V | C | TEMP AEROCDSR MOITIE 1ER RANGEE | Y | Y | 00:01 | 20454 | RGV10MAG51CT501_XQ50
BE-PSG_D_0101_CON_01_O_W_1_Perc | D_0101_CON_01_O_W_1_Perc | BE-PSG_0101_CON | CON_01_O_W_1_Perc | BE-PSG | CON | D_0101_CON_01_O_W_1_Perc | D | 0101 | CON | 01 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG11-AA130M-XS0 | Bin | VN SORT RANGEE 1 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_CON_02L_T_S_1_C | D_0101_CON_02L_T_S_1_C | BE-PSG_0101_CON | CON_02L_T_S_1_C | BE-PSG | CON | D_0101_CON_02L_T_S_1_C | D | 0101 | CON | 02L | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG12-CT502-X1V | C | TEMP AEROCDSR MOITIE 2EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ52CT502_XQ50
BE-PSG_D_0101_CON_02R_T_S_1_C | D_0101_CON_02R_T_S_1_C | BE-PSG_0101_CON | CON_02R_T_S_1_C | BE-PSG | CON | D_0101_CON_02R_T_S_1_C | D | 0101 | CON | 02R | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG12-CT501-X1V | C | TEMP AEROCDSR MOITIE 2EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ52CT501_XQ50
BE-PSG_D_0101_CON_03L_T_S_1_C | D_0101_CON_03L_T_S_1_C | BE-PSG_0101_CON | CON_03L_T_S_1_C | BE-PSG | CON | D_0101_CON_03L_T_S_1_C | D | 0101 | CON | 03L | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG13-CT502-X1V | C | TEMP AEROCDSR MOITIE 3EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ53CT502_XQ50
BE-PSG_D_0101_CON_03R_T_S_1_C | D_0101_CON_03R_T_S_1_C | BE-PSG_0101_CON | CON_03R_T_S_1_C | BE-PSG | CON | D_0101_CON_03R_T_S_1_C | D | 0101 | CON | 03R | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG13-CT501-X1V | C | TEMP AEROCDSR MOITIE 3EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ53CT501_XQ50
BE-PSG_D_0101_CON_04L_T_S_1_C | D_0101_CON_04L_T_S_1_C | BE-PSG_0101_CON | CON_04L_T_S_1_C | BE-PSG | CON | D_0101_CON_04L_T_S_1_C | D | 0101 | CON | 04L | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG14-CT502-X1V | C | TEMP AEROCDSR MOITIE 4EME RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ54CT502_XQ50
BE-PSG_D_0101_CON_04R_T_S_1_C | D_0101_CON_04R_T_S_1_C | BE-PSG_0101_CON | CON_04R_T_S_1_C | BE-PSG | CON | D_0101_CON_04R_T_S_1_C | D | 0101 | CON | 04R | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-MAG14-CT501-X1V | C | TEMP AEROCDSR MOITIE 4EME RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ54CT501_XQ50
BE-PSG_D_0101_CON_04_O_W_1_Perc | D_0101_CON_04_O_W_1_Perc | BE-PSG_0101_CON | CON_04_O_W_1_Perc | BE-PSG | CON | D_0101_CON_04_O_W_1_Perc | D | 0101 | CON | 04 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG14-AA130M-XS0 | Bin | VN SORT RANGEE 4 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_01C_T_W_1_C | D_0101_HDP_01C_T_W_1_C | BE-PSG_0101_VAS | HDP_01C_T_W_1_C | BE-PSG | VAS | D_0101_HDP_01C_T_W_1_C | D | 0101 | HDP | 01C | T | W | 1 | C | piatlas.myengie.com | BE-PSG-01-MAJ61-CT501-X1V | C | TEMP EAU SORTIE AEROREFRIGERANT | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_01P_O_A_1_Perc | D_0101_HDP_01P_O_A_1_Perc | BE-PSG_0101_VAS | HDP_01P_O_A_1_Perc | BE-PSG | VAS | D_0101_HDP_01P_O_A_1_Perc | D | 0101 | HDP | 01P | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ21-AA120M-XS0 | Bin | VM EJECT GAV PVC 1 - FERME | N | N | 00:01 | 20454
BE-PSG_D_0101_HDP_01R_T_W_1_C | D_0101_HDP_01R_T_W_1_C | BE-PSG_0101_VAS | HDP_01R_T_W_1_C | BE-PSG | VAS | D_0101_HDP_01R_T_W_1_C | D | 0101 | HDP | 01R | T | W | 1 | C | piatlas.myengie.com | BE-PSG-01-MAJ21-CT501-X1V | C | TEMP EAU CIRCUL PVC 1 | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_01S_O_A_1_Perc | D_0101_HDP_01S_O_A_1_Perc | BE-PSG_0101_VAS | HDP_01S_O_A_1_Perc | BE-PSG | VAS | D_0101_HDP_01S_O_A_1_Perc | D | 0101 | HDP | 01S | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ16-AA100M-XS0 | Bin | VM ASPIRATION PVC 1 - FERME | N | N | 00:01 | 20454
BE-PSG_D_0101_HDP_01_S_X_1_Perc | D_0101_HDP_01_S_X_1_Perc | BE-PSG_0101_VAS | HDP_01_S_X_1_Perc | BE-PSG | VAS | D_0101_HDP_01_S_X_1_Perc | D | 0101 | HDP | 01 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ21-AP010-XA0 | Bin | POMPE A VIDE 1 - HS-SERV | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_02C_T_W_1_C | D_0101_HDP_02C_T_W_1_C | BE-PSG_0101_VAS | HDP_02C_T_W_1_C | BE-PSG | VAS | D_0101_HDP_02C_T_W_1_C | D | 0101 | HDP | 02C | T | W | 1 | C | piatlas.myengie.com | BE-PSG-01-MAJ82-CT501-X1V | C | TEMP EAU ENTREE AEROREFRIGERANT | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_02P_O_A_1_Perc | D_0101_HDP_02P_O_A_1_Perc | BE-PSG_0101_VAS | HDP_02P_O_A_1_Perc | BE-PSG | VAS | D_0101_HDP_02P_O_A_1_Perc | D | 0101 | HDP | 02P | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ22-AA120M-XS0 | Bin | VM EJECT GAV PVC 2 - FERME | N | N | 00:01 | 20454
BE-PSG_D_0101_HDP_02_S_X_1_Perc | D_0101_HDP_02_S_X_1_Perc | BE-PSG_0101_VAS | HDP_02_S_X_1_Perc | BE-PSG | VAS | D_0101_HDP_02_S_X_1_Perc | D | 0101 | HDP | 02 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ22-AP010-XA0 | Bin | POMPE A VIDE 2 - HS-SERV | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HDP_02_T_W_1_C | D_0101_HDP_02_T_W_1_C | BE-PSG_0101_VAS | HDP_02_T_W_1_C | BE-PSG | VAS | D_0101_HDP_02_T_W_1_C | D | 0101 | HDP | 02 | T | W | 1 | C | piatlas.myengie.com | BE-PSG-01-MAJ22-CT501-X1V | C | TEMP EAU CIRCUL PVC 2 | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HGE_01M_O_A_1_Perc | D_0101_HGE_01M_O_A_1_Perc | BE-PSG_0101_VAS | HGE_01M_O_A_1_Perc | BE-PSG | VAS | D_0101_HGE_01M_O_A_1_Perc | D | 0101 | HGE | 01M | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ32-CG100A-XS0 | Bin | ETAT EV VAP SECON EJECT -FERME | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HGE_01M_T_A_1_C | D_0101_HGE_01M_T_A_1_C | BE-PSG_0101_VAS | HGE_01M_T_A_1_C | BE-PSG | VAS | D_0101_HGE_01M_T_A_1_C | D | 0101 | HGE | 01M | T | A | 1 | C | piatlas.myengie.com | BE-PSG-01-MAJ32-CT501-X1V | C | TEMP SORTIE PURGEUR MAJ32AA406F | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HGE_01S_O_A_1_Perc | D_0101_HGE_01S_O_A_1_Perc | BE-PSG_0101_VAS | HGE_01S_O_A_1_Perc | BE-PSG | VAS | D_0101_HGE_01S_O_A_1_Perc | D | 0101 | HGE | 01S | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ30-AA100M-XS0 | Bin | VM AIR EXTRAC EJECT - FERME | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_HGE_02M_O_A_1_Perc | D_0101_HGE_02M_O_A_1_Perc | BE-PSG_0101_VAS | HGE_02M_O_A_1_Perc | BE-PSG | VAS | D_0101_HGE_02M_O_A_1_Perc | D | 0101 | HGE | 02M | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ33-AA100M-XS0 | Bin | VM VAP EJECT PRIM - FERME | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_IVS_01_O_S_1_Perc | D_0101_IVS_01_O_S_1_Perc | BE-PSG_0101_IV3 | IVS_01_O_S_1_Perc | BE-PSG | IV3 | D_0101_IVS_01_O_S_1_Perc | D | 0101 | IVS | 01 | O | S | 1 | Perc | piatlas.myengie.com | BE-PSG-01-LBS11-AA100M-XS0 | Bin | VN ENTR RANGEE 1 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_IVS_04_O_S_1_Perc | D_0101_IVS_04_O_S_1_Perc | BE-PSG_0101_IV3 | IVS_04_O_S_1_Perc | BE-PSG | IV3 | D_0101_IVS_04_O_S_1_Perc | D | 0101 | IVS | 04 | O | S | 1 | Perc | piatlas.myengie.com | BE-PSG-01-LBS14-AA100M-XS0 | Bin | VN ENTR RANGEE 4 AERO - FERME | N | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_MOT_0101_S_X_1_Perc | D_0101_MOT_0101_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0101_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0101_S_X_1_Perc | D | 0101 | MOT | 0101 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN011-XA0 | Bin | VENTIL 11 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0101_S_X_2_Perc | D_0101_MOT_0101_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0101_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0101_S_X_2_Perc | D | 0101 | MOT | 0101 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN011-XA1 | Bin | VENTIL 11 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0102_S_X_1_Perc | D_0101_MOT_0102_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0102_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0102_S_X_1_Perc | D | 0101 | MOT | 0102 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN012-XA0 | Bin | VENTIL 12 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0102_S_X_2_Perc | D_0101_MOT_0102_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0102_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0102_S_X_2_Perc | D | 0101 | MOT | 0102 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN012-XA1 | Bin | VENTIL 12 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0103_S_X_1_Perc | D_0101_MOT_0103_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0103_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0103_S_X_1_Perc | D | 0101 | MOT | 0103 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN013-XA0 | Bin | VENTIL 13 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0103_S_X_2_Perc | D_0101_MOT_0103_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0103_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0103_S_X_2_Perc | D | 0101 | MOT | 0103 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN013-XA1 | Bin | VENTIL 13 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0104_S_X_1_Perc | D_0101_MOT_0104_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0104_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0104_S_X_1_Perc | D | 0101 | MOT | 0104 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN014-XA0 | Bin | VENTIL 14 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0104_S_X_2_Perc | D_0101_MOT_0104_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0104_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0104_S_X_2_Perc | D | 0101 | MOT | 0104 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN014-XA1 | Bin | VENTIL 14 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0105_S_X_1_Perc | D_0101_MOT_0105_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0105_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0105_S_X_1_Perc | D | 0101 | MOT | 0105 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN015-XA0 | Bin | VENTIL 15 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0105_S_X_2_Perc | D_0101_MOT_0105_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0105_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0105_S_X_2_Perc | D | 0101 | MOT | 0105 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN015-XA1 | Bin | VENTIL 15 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0106_S_X_1_Perc | D_0101_MOT_0106_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0106_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0106_S_X_1_Perc | D | 0101 | MOT | 0106 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN016-XA0 | Bin | VENTIL 16 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0106_S_X_2_Perc | D_0101_MOT_0106_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0106_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0106_S_X_2_Perc | D | 0101 | MOT | 0106 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN016-XA1 | Bin | VENTIL 16 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0201_S_X_1_Perc | D_0101_MOT_0201_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0201_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0201_S_X_1_Perc | D | 0101 | MOT | 0201 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN021-XA0 | Bin | VENTIL 21 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0201_S_X_2_Perc | D_0101_MOT_0201_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0201_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0201_S_X_2_Perc | D | 0101 | MOT | 0201 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN021-XA1 | Bin | VENTIL 21 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0202_S_X_1_Perc | D_0101_MOT_0202_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0202_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0202_S_X_1_Perc | D | 0101 | MOT | 0202 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN022-XA0 | Bin | VENTIL 22 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0202_S_X_2_Perc | D_0101_MOT_0202_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0202_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0202_S_X_2_Perc | D | 0101 | MOT | 0202 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN022-XA1 | Bin | VENTIL 22 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0203_S_X_1_Perc | D_0101_MOT_0203_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0203_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0203_S_X_1_Perc | D | 0101 | MOT | 0203 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN023-XA0 | Bin | VENTIL 23 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0203_S_X_2_Perc | D_0101_MOT_0203_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0203_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0203_S_X_2_Perc | D | 0101 | MOT | 0203 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN023-XA1 | Bin | VENTIL 23 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0204_S_X_1_Perc | D_0101_MOT_0204_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0204_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0204_S_X_1_Perc | D | 0101 | MOT | 0204 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN024-XA0 | Bin | VENTIL 24 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0204_S_X_2_Perc | D_0101_MOT_0204_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0204_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0204_S_X_2_Perc | D | 0101 | MOT | 0204 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN024-XA1 | Bin | VENTIL 24 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0205_S_X_1_Perc | D_0101_MOT_0205_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0205_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0205_S_X_1_Perc | D | 0101 | MOT | 0205 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN025-XA0 | Bin | VENTIL 25 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0205_S_X_2_Perc | D_0101_MOT_0205_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0205_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0205_S_X_2_Perc | D | 0101 | MOT | 0205 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN025-XA1 | Bin | VENTIL 25 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0206_S_X_1_Perc | D_0101_MOT_0206_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0206_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0206_S_X_1_Perc | D | 0101 | MOT | 0206 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN026-XA0 | Bin | VENTIL 26 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0206_S_X_2_Perc | D_0101_MOT_0206_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0206_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0206_S_X_2_Perc | D | 0101 | MOT | 0206 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN026-XA1 | Bin | VENTIL 26 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0301_S_X_1_Perc | D_0101_MOT_0301_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0301_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0301_S_X_1_Perc | D | 0101 | MOT | 0301 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN031-XA0 | Bin | VENTIL 31 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0301_S_X_2_Perc | D_0101_MOT_0301_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0301_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0301_S_X_2_Perc | D | 0101 | MOT | 0301 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN031-XA1 | Bin | VENTIL 31 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0302_S_X_1_Perc | D_0101_MOT_0302_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0302_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0302_S_X_1_Perc | D | 0101 | MOT | 0302 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN032-XA0 | Bin | VENTIL 32 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0302_S_X_2_Perc | D_0101_MOT_0302_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0302_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0302_S_X_2_Perc | D | 0101 | MOT | 0302 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN032-XA1 | Bin | VENTIL 32 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0303_S_X_1_Perc | D_0101_MOT_0303_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0303_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0303_S_X_1_Perc | D | 0101 | MOT | 0303 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN033-XA0 | Bin | VENTIL 33 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0303_S_X_2_Perc | D_0101_MOT_0303_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0303_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0303_S_X_2_Perc | D | 0101 | MOT | 0303 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN033-XA1 | Bin | VENTIL 33 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0304_S_X_1_Perc | D_0101_MOT_0304_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0304_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0304_S_X_1_Perc | D | 0101 | MOT | 0304 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN034-XA0 | Bin | VENTIL 34 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0304_S_X_2_Perc | D_0101_MOT_0304_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0304_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0304_S_X_2_Perc | D | 0101 | MOT | 0304 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN034-XA1 | Bin | VENTIL 34 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0305_S_X_1_Perc | D_0101_MOT_0305_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0305_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0305_S_X_1_Perc | D | 0101 | MOT | 0305 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN035-XA0 | Bin | VENTIL 35 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0305_S_X_2_Perc | D_0101_MOT_0305_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0305_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0305_S_X_2_Perc | D | 0101 | MOT | 0305 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN035-XA1 | Bin | VENTIL 35 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0306_S_X_1_Perc | D_0101_MOT_0306_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0306_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0306_S_X_1_Perc | D | 0101 | MOT | 0306 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN036-XA0 | Bin | VENTIL 36 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0306_S_X_2_Perc | D_0101_MOT_0306_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0306_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0306_S_X_2_Perc | D | 0101 | MOT | 0306 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN036-XA1 | Bin | VENTIL 36 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0401_S_X_1_Perc | D_0101_MOT_0401_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0401_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0401_S_X_1_Perc | D | 0101 | MOT | 0401 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN041-XA0 | Bin | VENTIL 41 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0401_S_X_2_Perc | D_0101_MOT_0401_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0401_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0401_S_X_2_Perc | D | 0101 | MOT | 0401 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN041-XA1 | Bin | VENTIL 41 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0402_S_X_1_Perc | D_0101_MOT_0402_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0402_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0402_S_X_1_Perc | D | 0101 | MOT | 0402 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN042-XA0 | Bin | VENTIL 42 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0402_S_X_2_Perc | D_0101_MOT_0402_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0402_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0402_S_X_2_Perc | D | 0101 | MOT | 0402 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN042-XA1 | Bin | VENTIL 42 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0403_S_X_1_Perc | D_0101_MOT_0403_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0403_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0403_S_X_1_Perc | D | 0101 | MOT | 0403 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN043-XA0 | Bin | VENTIL 43 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0403_S_X_2_Perc | D_0101_MOT_0403_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0403_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0403_S_X_2_Perc | D | 0101 | MOT | 0403 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN043-XA1 | Bin | VENTIL 43 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0404_S_X_1_Perc | D_0101_MOT_0404_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0404_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0404_S_X_1_Perc | D | 0101 | MOT | 0404 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN044-XA0 | Bin | VENTIL 44 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0404_S_X_2_Perc | D_0101_MOT_0404_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0404_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0404_S_X_2_Perc | D | 0101 | MOT | 0404 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN044-XA1 | Bin | VENTIL 44 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0405_S_X_1_Perc | D_0101_MOT_0405_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0405_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0405_S_X_1_Perc | D | 0101 | MOT | 0405 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN045-XA0 | Bin | VENTIL 45 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0405_S_X_2_Perc | D_0101_MOT_0405_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0405_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0405_S_X_2_Perc | D | 0101 | MOT | 0405 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN045-XA1 | Bin | VENTIL 45 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0406_S_X_1_Perc | D_0101_MOT_0406_S_X_1_Perc | BE-PSG_0101_MOT | MOT_0406_S_X_1_Perc | BE-PSG | MOT | D_0101_MOT_0406_S_X_1_Perc | D | 0101 | MOT | 0406 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN046-XA0 | Bin | VENTIL 46 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MOT_0406_S_X_2_Perc | D_0101_MOT_0406_S_X_2_Perc | BE-PSG_0101_MOT | MOT_0406_S_X_2_Perc | BE-PSG | MOT | D_0101_MOT_0406_S_X_2_Perc | D | 0101 | MOT | 0406 | S | X | 2 | Perc | piatlas.myengie.com | BE-PSG-01-MAG10-AN046-XA1 | Bin | VENTIL 46 AEROCDSR - SIGNAL HORS | Y | Y | 00:01 | 20454
BE-PSG_D_0101_MUL_01_O_W_1_Perc | D_0101_MUL_01_O_W_1_Perc | BE-PSG_0101_OL3 | MUL_01_O_W_1_Perc | BE-PSG | OL3 | D_0101_MUL_01_O_W_1_Perc | D | 0101 | MUL | 01 | O | W | 1 | Perc | piatlas.myengie.com | BE-PSG-01-LCB50-CG110C-X1V | Perc | POS VR APP BAC RECUP CONDEN | N | N | 00:01 | 20454
BE-PSG_D_0101_PCO_01_F_X_1_ton_h | D_0101_PCO_01_F_X_1_ton_h | BE-PSG_0101_ACO | PCO_01_F_X_1_ton_h | BE-PSG | ACO | D_0101_PCO_01_F_X_1_ton_h | D | 0101 | PCO | 01 | F | X | 1 | ton_h | piatlas.myengie.com | BE-PSG-01-MBM10-CF504-XC7 | ton_h | DEBIT INJECTION EAU TG | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_F_X_2_ton_h | D_0101_PCO_01_F_X_2_ton_h | BE-PSG_0101_ACO | PCO_01_F_X_2_ton_h | BE-PSG | ACO | D_0101_PCO_01_F_X_2_ton_h | D | 0101 | PCO | 01 | F | X | 2 | ton_h | piatlas.myengie.com | BE-PSG-01-MBM10-CF505-X2V | ton_h | DEBIT ARROSAGE AERO - 1/2 | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_F_X_3_ton_h | D_0101_PCO_01_F_X_3_ton_h | BE-PSG_0101_ACO | PCO_01_F_X_3_ton_h | BE-PSG | ACO | D_0101_PCO_01_F_X_3_ton_h | D | 0101 | PCO | 01 | F | X | 3 | ton_h | piatlas.myengie.com | BE-PSG-01-MBM10-CF506-X1V | ton_h | DEBIT INJECTION EAU AERO | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_F_X_4_ton_h | D_0101_PCO_01_F_X_4_ton_h | BE-PSG_0101_ACO | PCO_01_F_X_4_ton_h | BE-PSG | ACO | D_0101_PCO_01_F_X_4_ton_h | D | 0101 | PCO | 01 | F | X | 4 | ton_h | piatlas.myengie.com | BE-PSG-01-MBM10-CF507-X1V | ton_h | DEBIT INJECTION EAU AERO | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_I_X_1_A | D_0101_PCO_01_I_X_1_A | BE-PSG_0101_ACO | PCO_01_I_X_1_A | BE-PSG | ACO | D_0101_PCO_01_I_X_1_A | D | 0101 | PCO | 01 | I | X | 1 | A | piatlas.myengie.com | BE-PSG-01-MBM10-CE202B-XC7 | A | INTENSITE POMPE INJ EAU | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_P_X_1_bar | D_0101_PCO_01_P_X_1_bar | BE-PSG_0101_ACO | PCO_01_P_X_1_bar | BE-PSG | ACO | D_0101_PCO_01_P_X_1_bar | D | 0101 | PCO | 01 | P | X | 1 | bar | piatlas.myengie.com | BE-PSG-01-MBM10-CP504-X1V | bar | PRESSION EAU ARROSAGE AERO | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PCO_01_S_X_1_Perc | D_0101_PCO_01_S_X_1_Perc | BE-PSG_0101_ACO | PCO_01_S_X_1_Perc | BE-PSG | ACO | D_0101_PCO_01_S_X_1_Perc | D | 0101 | PCO | 01 | S | X | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MBM10-AP002-XA0 | Bin | POMPE INJEC EAU AERO - HS-SERV | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_PPA_01_W_X_1_MW | D_0101_PPA_01_W_X_1_MW | BE-PSG_0101_UNT | PPA_01_W_X_1_MW | BE-PSG | UNT | D_0101_PPA_01_W_X_1_MW | D | 0101 | PPA | 01 | W | X | 1 | MW | piatlas.myengie.com | BE-PSG-01-BAA10-CE301P-X1V | MW | PUISSANCE ACTIVE BRUTE | Y | Y | 00:01 | 20454 | RGV_T1_DWATT1
BE-PSG_D_0101_QAT_01_O_A_1_Perc | D_0101_QAT_01_O_A_1_Perc | BE-PSG_0101_ATL | QAT_01_O_A_1_Perc | BE-PSG | ATL | D_0101_QAT_01_O_A_1_Perc | D | 0101 | QAT | 01 | O | A | 1 | Perc | piatlas.myengie.com | BE-PSG-01-MAJ15-AA101M-XS0 | Bin | VM ISOL GAINE - FERME | Y | Y | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_SEC_01L_T_S_3_C | D_0101_SEC_01L_T_S_3_C | BE-PSG_0101_ATL | SEC_01L_T_S_3_C | BE-PSG | ATL | D_0101_SEC_01L_T_S_3_C | D | 0101 | SEC | 01L | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ11-CT501-X1V | C | TEMP AIR SORT MOITIE 1ER RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ51CT501_XQ50
BE-PSG_D_0101_SEC_01R_T_S_3_C | D_0101_SEC_01R_T_S_3_C | BE-PSG_0101_ATL | SEC_01R_T_S_3_C | BE-PSG | ATL | D_0101_SEC_01R_T_S_3_C | D | 0101 | SEC | 01R | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ11-CT502-X1V | C | TEMP AIR SORT MOITIE 1ER RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ51CT502_XQ50
BE-PSG_D_0101_SEC_02L_T_S_3_C | D_0101_SEC_02L_T_S_3_C | BE-PSG_0101_ATL | SEC_02L_T_S_3_C | BE-PSG | ATL | D_0101_SEC_02L_T_S_3_C | D | 0101 | SEC | 02L | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ12-CT501-X1V | C | TEMP AIR SORT MOITIE 2EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ52CT501_XQ50
BE-PSG_D_0101_SEC_02R_T_S_3_C | D_0101_SEC_02R_T_S_3_C | BE-PSG_0101_ATL | SEC_02R_T_S_3_C | BE-PSG | ATL | D_0101_SEC_02R_T_S_3_C | D | 0101 | SEC | 02R | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ12-CT502-X1V | C | TEMP AIR SORT MOITIE 2EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ52CT502_XQ50
BE-PSG_D_0101_SEC_03L_T_S_3_C | D_0101_SEC_03L_T_S_3_C | BE-PSG_0101_ATL | SEC_03L_T_S_3_C | BE-PSG | ATL | D_0101_SEC_03L_T_S_3_C | D | 0101 | SEC | 03L | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ13-CT501-X1V | C | TEMP AIR SORT MOITIE 3EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ53CT501_XQ50
BE-PSG_D_0101_SEC_03R_T_S_3_C | D_0101_SEC_03R_T_S_3_C | BE-PSG_0101_ATL | SEC_03R_T_S_3_C | BE-PSG | ATL | D_0101_SEC_03R_T_S_3_C | D | 0101 | SEC | 03R | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ13-CT502-X1V | C | TEMP AIR SORT MOITIE 3EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ53CT502_XQ50
BE-PSG_D_0101_SEC_04L_T_S_3_C | D_0101_SEC_04L_T_S_3_C | BE-PSG_0101_ATL | SEC_04L_T_S_3_C | BE-PSG | ATL | D_0101_SEC_04L_T_S_3_C | D | 0101 | SEC | 04L | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ14-CT501-X1V | C | TEMP AIR SORT MOITIE 4EM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ54CT501_XQ50
BE-PSG_D_0101_SEC_04R_T_S_3_C | D_0101_SEC_04R_T_S_3_C | BE-PSG_0101_ATL | SEC_04R_T_S_3_C | BE-PSG | ATL | D_0101_SEC_04R_T_S_3_C | D | 0101 | SEC | 04R | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-MAJ14-CT502-X1V | C | TEMP AIR SORT MOITIE AEM RANGEE | Y | Y | 00:01 | 20454 | RGV10MAJ54CT502_XQ50
BE-PSG_D_0101_STE_01_F_S_1_ton_h | D_0101_STE_01_F_S_1_ton_h | BE-PSG_0101_STE | STE_01_F_S_1_ton_h | BE-PSG | STE | D_0101_STE_01_F_S_1_ton_h | D | 0101 | STE | 01 | F | S | 1 | ton_h | piatlas.myengie.com | BE-PSG-01-HAG25-CF601-X3V | t/h | DEBIT MOYEN VAP BP SATUREE - 2/3 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_F_S_2_ton_h | D_0101_STE_01_F_S_2_ton_h | BE-PSG_0101_STE | STE_01_F_S_2_ton_h | BE-PSG | STE | D_0101_STE_01_F_S_2_ton_h | D | 0101 | STE | 01 | F | S | 2 | ton_h | piatlas.myengie.com | BE-PSG-01-HAG40-CF601-X3V | t/h | DEB MOYEN VAP SATUREE MP - 2/3 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_F_S_3_ton_h | D_0101_STE_01_F_S_3_ton_h | BE-PSG_0101_STE | STE_01_F_S_3_ton_h | BE-PSG | STE | D_0101_STE_01_F_S_3_ton_h | D | 0101 | STE | 01 | F | S | 3 | ton_h | piatlas.myengie.com | BE-PSG-01-HAG80-CF601-X3V | t/h | DEBIT MOYEN VAP HP - 2/3 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_F_S_4_ton_h | D_0101_STE_01_F_S_4_ton_h | BE-PSG_0101_STE | STE_01_F_S_4_ton_h | BE-PSG | STE | D_0101_STE_01_F_S_4_ton_h | D | 0101 | STE | 01 | F | S | 4 | ton_h | piatlas.myengie.com | BE-PSG-01-HAG00-EU901-X5V | t/h | DEBIT VAPEUR HP + MP + BP | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_F_S_5_ton_h | D_0101_STE_01_F_S_5_ton_h | BE-PSG_0101_STE | STE_01_F_S_5_ton_h | BE-PSG | STE | D_0101_STE_01_F_S_5_ton_h | D | 0101 | STE | 01 | F | S | 5 | ton_h | piatlas.myengie.com | BE-PSG-01-HAG00-EU903-X5V | t/h | DEBIT VAPEUR TOTAL POUR SUIVI MAG | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_P_S_1_mbar | D_0101_STE_01_P_S_1_mbar | BE-PSG_0101_STE | STE_01_P_S_1_mbar | BE-PSG | STE | D_0101_STE_01_P_S_1_mbar | D | 0101 | STE | 01 | P | S | 1 | mbar | piatlas.myengie.com | BE-PSG-01-LBS10-CP501-X31V | mbar | PRES VAP GAINE ECHP TV - 1/3_2 | N | N | 00:01 | 20454 | RGV10MAC30CP510_XQ50/RGV10LBS50CP501_XJ51
BE-PSG_D_0101_STE_01_P_S_2_mbar | D_0101_STE_01_P_S_2_mbar | BE-PSG_0101_STE | STE_01_P_S_2_mbar | BE-PSG | STE | D_0101_STE_01_P_S_2_mbar | D | 0101 | STE | 01 | P | S | 2 | mbar | piatlas.myengie.com | BE-PSG-01-LBS10-CP501-X32V | mbar | PRES VAP GAINE ECHP TV - 2/3_2 | N | N | 00:01 | 20454
BE-PSG_D_0101_STE_01_P_S_3_mbar | D_0101_STE_01_P_S_3_mbar | BE-PSG_0101_STE | STE_01_P_S_3_mbar | BE-PSG | STE | D_0101_STE_01_P_S_3_mbar | D | 0101 | STE | 01 | P | S | 3 | mbar | piatlas.myengie.com | BE-PSG-01-LBS10-CP501-X33V | mbar | PRES VAP GAINE ECHP TV - 2/3_3 | N | N | 00:01 | 20454
BE-PSG_D_0101_STE_01_T_S_1_C | D_0101_STE_01_T_S_1_C | BE-PSG_0101_STE | STE_01_T_S_1_C | BE-PSG | STE | D_0101_STE_01_T_S_1_C | D | 0101 | STE | 01 | T | S | 1 | C | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X31V | C | TEMPERATURE VAP GAINE - 1/3_1 | Y | Y | 00:01 | 20454 | RGV10MAC30CT540AXQ50
BE-PSG_D_0101_STE_01_T_S_1_K | D_0101_STE_01_T_S_1_K | BE-PSG_0101_STE | STE_01_T_S_1_K | BE-PSG | STE | D_0101_STE_01_T_S_1_K | D | 0101 | STE | 01 | T | S | 1 | K | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X31V | C | TEMPERATURE VAP GAINE - 1/3_1 | Y | Y | 00:01 | 20454 | RGV10MAC30CT540AXQ50
BE-PSG_D_0101_STE_01_T_S_2_C | D_0101_STE_01_T_S_2_C | BE-PSG_0101_STE | STE_01_T_S_2_C | BE-PSG | STE | D_0101_STE_01_T_S_2_C | D | 0101 | STE | 01 | T | S | 2 | C | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X32V | C | TEMPERATURE VAP GAINE - 2/3_2 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_T_S_2_K | D_0101_STE_01_T_S_2_K | BE-PSG_0101_STE | STE_01_T_S_2_K | BE-PSG | STE | D_0101_STE_01_T_S_2_K | D | 0101 | STE | 01 | T | S | 2 | K | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X32V | C | TEMPERATURE VAP GAINE - 2/3_2 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_T_S_3_C | D_0101_STE_01_T_S_3_C | BE-PSG_0101_STE | STE_01_T_S_3_C | BE-PSG | STE | D_0101_STE_01_T_S_3_C | D | 0101 | STE | 01 | T | S | 3 | C | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X33V | C | TEMPERATURE VAP GAINE - 2/3_3 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_T_S_3_K | D_0101_STE_01_T_S_3_K | BE-PSG_0101_STE | STE_01_T_S_3_K | BE-PSG | STE | D_0101_STE_01_T_S_3_K | D | 0101 | STE | 01 | T | S | 3 | K | piatlas.myengie.com | BE-PSG-01-LBS10-CT501-X33V | C | TEMPERATURE VAP GAINE - 2/3_3 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_STE_01_W_X_1_MW | D_0101_STE_01_W_X_1_MW | BE-PSG_0101_STE | STE_01_W_X_1_MW | BE-PSG | STE | D_0101_STE_01_W_X_1_MW | D | 0101 | STE | 01 | W | X | 1 | MW | piatlas.myengie.com | BE-PSG-01-CK00-EU902-X1V | MW | PUISSANCE TV CALCULEE | Y | N | 00:01 | 20454 | not in Gent
BE-PSG_D_0101_CDT_01_T_W_1_C | D_0101_CDT_01_T_W_1_C | BE-PSG_0101_CDT | CDT_01_T_W_1_C | BE-PSG | CDT | D_0101_CDT_01_T_W_1_C | D | 0101 | CDT | 01 | T | W | 1 | C | piatlas.myengie.com | BE-PSG-01-LCB32-CT501A-X1V | C | TEMPERATURE CONDENSATE-1 | Y | Y | 00:01 | 20454
BE-PSG_D_0101_CDT_01_T_W_2_C | D_0101_CDT_01_T_W_2_C | BE-PSG_0101_CDT | CDT_01_T_W_2_C | BE-PSG | CDT | D_0101_CDT_01_T_W_2_C | D | 0101 | CDT | 01 | T | W | 2 | C | piatlas.myengie.com | BE-PSG-01-LCB32-CT501B-X1V | C | TEMPERATURE CONDENSATE-2 | Y | Y | 00:01 | 20454
BE-PSG_I_0101_MGE_0101HSGSGMF_A_X_1_mm_s | I_0101_MGE_0101HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0101HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | Y
BE-PSG_I_0101_MGE_0101HSGSSER1_A_X_1_ | I_0101_MGE_0101HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101HSGSSER1_A_X_1_ | I | 0101 | MGE | 0101HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0101HSGSSER2_A_X_1_ | I_0101_MGE_0101HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101HSGSSER2_A_X_1_ | I | 0101 | MGE | 0101HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0101HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0101HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0101HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0101HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBSF_A_X_1_mm_s | I_0101_MGE_0101HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0101HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRFTF_A_X_1_mm_s | I_0101_MGE_0101HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0101HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0101HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0101HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0101HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0101HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBSF_A_X_2_mm_s | I_0101_MGE_0101HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0101HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRFTF_A_X_2_mm_s | I_0101_MGE_0101HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0101HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0101HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0101HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0101HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0101HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRBSF_A_X_3_mm_s | I_0101_MGE_0101HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0101HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSBRFTF_A_X_3_mm_s | I_0101_MGE_0101HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0101HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSHB_V_X_1_G | I_0101_MGE_0101HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101HSHB_V_X_1_G | I | 0101 | MGE | 0101HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0101HSLO_A_X_1_mm_s | I_0101_MGE_0101HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101HSLO_A_X_1_mm_s | I | 0101 | MGE | 0101HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101HSLB_V_X_1_G | I_0101_MGE_0101HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101HSLB_V_X_1_G | I | 0101 | MGE | 0101HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0101HSAMP_K_X_1_ | I_0101_MGE_0101HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0101HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0101HSAMP_K_X_1_ | I | 0101 | MGE | 0101HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_S1Amp1_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSGMF_A_X_1_mm_s | I_0101_MGE_0101IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0101IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSSER1_A_X_1_ | I_0101_MGE_0101IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101IMGSSER1_A_X_1_ | I | 0101 | MGE | 0101IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSSER2_A_X_1_ | I_0101_MGE_0101IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101IMGSSER2_A_X_1_ | I | 0101 | MGE | 0101IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSGMF_A_X_2_mm_s | I_0101_MGE_0101IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0101IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSSER1_A_X_2_ | I_0101_MGE_0101IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0101IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0101IMGSSER1_A_X_2_ | I | 0101 | MGE | 0101IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0101IMGSSER2_A_X_2_ | I_0101_MGE_0101IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0101IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0101IMGSSER2_A_X_2_ | I | 0101 | MGE | 0101IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0101IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0101IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0101IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0101IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBSF_A_X_1_mm_s | I_0101_MGE_0101IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0101IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRFTF_A_X_1_mm_s | I_0101_MGE_0101IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0101IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0101IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0101IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0101IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0101IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRBSF_A_X_2_mm_s | I_0101_MGE_0101IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0101IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMBRFTF_A_X_2_mm_s | I_0101_MGE_0101IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0101IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMHB_V_X_1_G | I_0101_MGE_0101IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101IMHB_V_X_1_G | I | 0101 | MGE | 0101IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0101IMLO_A_X_1_mm_s | I_0101_MGE_0101IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101IMLO_A_X_1_mm_s | I | 0101 | MGE | 0101IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101IMLB_V_X_1_G | I_0101_MGE_0101IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101IMLB_V_X_1_G | I | 0101 | MGE | 0101IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0101IMAMP_K_X_1_ | I_0101_MGE_0101IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0101IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0101IMAMP_K_X_1_ | I | 0101 | MGE | 0101IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_S1Amp3_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MGE_0101LSGSGMF_A_X_1_mm_s | I_0101_MGE_0101LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0101LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSGSSER1_A_X_1_ | I_0101_MGE_0101LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101LSGSSER1_A_X_1_ | I | 0101 | MGE | 0101LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0101LSGSSER2_A_X_1_ | I_0101_MGE_0101LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0101LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0101LSGSSER2_A_X_1_ | I | 0101 | MGE | 0101LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_1_mm_s | I_0101_MGE_0101LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_1_mm_s | I_0101_MGE_0101LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_2_mm_s | I_0101_MGE_0101LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_2_mm_s | I_0101_MGE_0101LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_3_mm_s | I_0101_MGE_0101LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_3_mm_s | I_0101_MGE_0101LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_4_mm_s | I_0101_MGE_0101LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_4_mm_s | I_0101_MGE_0101LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_5_mm_s | I_0101_MGE_0101LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_5_mm_s | I_0101_MGE_0101LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0101LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0101LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0101LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0101LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRBSF_A_X_6_mm_s | I_0101_MGE_0101LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0101LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSBRFTF_A_X_6_mm_s | I_0101_MGE_0101LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0101LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSHB_V_X_1_G | I_0101_MGE_0101LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101LSHB_V_X_1_G | I | 0101 | MGE | 0101LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0101LSLO_A_X_1_mm_s | I_0101_MGE_0101LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSLO_A_X_1_mm_s | I | 0101 | MGE | 0101LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSLB_V_X_1_G | I_0101_MGE_0101LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0101LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0101LSLB_V_X_1_G | I | 0101 | MGE | 0101LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0101LSUN_A_X_1_mm_s | I_0101_MGE_0101LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0101LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0101LSUN_A_X_1_mm_s | I | 0101 | MGE | 0101LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0101LSAMP_K_X_1_ | I_0101_MGE_0101LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0101LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0101LSAMP_K_X_1_ | I | 0101 | MGE | 0101LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaftt_S1Amp1_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MOT_0101MCHB_V_X_1_G | I_0101_MOT_0101MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0101MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0101MCHB_V_X_1_G | I | 0101 | MOT | 0101MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0101MCLO_A_X_1_mm_s | I_0101_MOT_0101MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCLO_A_X_1_mm_s | I | 0101 | MOT | 0101MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCLB_V_X_1_G | I_0101_MOT_0101MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0101MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0101MCLB_V_X_1_G | I | 0101 | MOT | 0101MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0101MCMA_A_X_1_mm_s | I_0101_MOT_0101MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCMA_A_X_1_mm_s | I | 0101 | MOT | 0101MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0101MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0101MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0101MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0101MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBSF_A_X_1_mm_s | I_0101_MOT_0101MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0101MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRFTF_A_X_1_mm_s | I_0101_MOT_0101MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0101MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0101MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0101MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0101MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0101MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRBSF_A_X_2_mm_s | I_0101_MOT_0101MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0101MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCBRFTF_A_X_2_mm_s | I_0101_MOT_0101MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0101MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MCAMP_K_X_1_ | I_0101_MOT_0101MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0101MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0101MCAMP_K_X_1_ | I | 0101 | MOT | 0101MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_S1Amp1_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MOT_0101MCUN_A_X_1_mm_s | I_0101_MOT_0101MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MCUN_A_X_1_mm_s | I | 0101 | MOT | 0101MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNHB_V_X_1_G | I_0101_MOT_0101MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0101MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0101MNHB_V_X_1_G | I | 0101 | MOT | 0101MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0101MNLO_A_X_1_mm_s | I_0101_MOT_0101MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNLO_A_X_1_mm_s | I | 0101 | MOT | 0101MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNLB_V_X_1_G | I_0101_MOT_0101MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0101MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0101MNLB_V_X_1_G | I | 0101 | MOT | 0101MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0101MNMA_A_X_1_mm_s | I_0101_MOT_0101MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNMA_A_X_1_mm_s | I | 0101 | MOT | 0101MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0101MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0101MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0101MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0101MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBSF_A_X_1_mm_s | I_0101_MOT_0101MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0101MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRFTF_A_X_1_mm_s | I_0101_MOT_0101MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0101MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0101MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0101MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0101MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0101MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRBSF_A_X_2_mm_s | I_0101_MOT_0101MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0101MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNBRFTF_A_X_2_mm_s | I_0101_MOT_0101MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0101MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0101MNAMP_K_X_1_ | I_0101_MOT_0101MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0101MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0101MNAMP_K_X_1_ | I | 0101 | MOT | 0101MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_S1Amp3_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MOT_0101MNUN_A_X_1_mm_s | I_0101_MOT_0101MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0101MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0101MNUN_A_X_1_mm_s | I | 0101 | MOT | 0101MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSGSGMF_A_X_1_mm_s | I_0101_MGE_0102HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0102HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSGSSER1_A_X_1_ | I_0101_MGE_0102HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102HSGSSER1_A_X_1_ | I | 0101 | MGE | 0102HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0102HSGSSER2_A_X_1_ | I_0101_MGE_0102HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102HSGSSER2_A_X_1_ | I | 0101 | MGE | 0102HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0102HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0102HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0102HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0102HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBSF_A_X_1_mm_s | I_0101_MGE_0102HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0102HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRFTF_A_X_1_mm_s | I_0101_MGE_0102HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0102HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0102HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0102HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0102HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0102HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBSF_A_X_2_mm_s | I_0101_MGE_0102HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0102HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRFTF_A_X_2_mm_s | I_0101_MGE_0102HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0102HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0102HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0102HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0102HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0102HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRBSF_A_X_3_mm_s | I_0101_MGE_0102HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0102HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSBRFTF_A_X_3_mm_s | I_0101_MGE_0102HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0102HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSHB_V_X_1_G | I_0101_MGE_0102HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102HSHB_V_X_1_G | I | 0101 | MGE | 0102HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0102HSLO_A_X_1_mm_s | I_0101_MGE_0102HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102HSLO_A_X_1_mm_s | I | 0101 | MGE | 0102HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102HSLB_V_X_1_G | I_0101_MGE_0102HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102HSLB_V_X_1_G | I | 0101 | MGE | 0102HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0102HSAMP_K_X_1_ | I_0101_MGE_0102HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0102HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0102HSAMP_K_X_1_ | I | 0101 | MGE | 0102HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaftt_S1Amp2_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSGMF_A_X_1_mm_s | I_0101_MGE_0102IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0102IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSSER1_A_X_1_ | I_0101_MGE_0102IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102IMGSSER1_A_X_1_ | I | 0101 | MGE | 0102IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSSER2_A_X_1_ | I_0101_MGE_0102IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102IMGSSER2_A_X_1_ | I | 0101 | MGE | 0102IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSGMF_A_X_2_mm_s | I_0101_MGE_0102IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0102IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSSER1_A_X_2_ | I_0101_MGE_0102IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0102IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0102IMGSSER1_A_X_2_ | I | 0101 | MGE | 0102IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0102IMGSSER2_A_X_2_ | I_0101_MGE_0102IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0102IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0102IMGSSER2_A_X_2_ | I | 0101 | MGE | 0102IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0102IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0102IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0102IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0102IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBSF_A_X_1_mm_s | I_0101_MGE_0102IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0102IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRFTF_A_X_1_mm_s | I_0101_MGE_0102IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0102IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0102IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0102IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0102IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0102IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRBSF_A_X_2_mm_s | I_0101_MGE_0102IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0102IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMBRFTF_A_X_2_mm_s | I_0101_MGE_0102IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0102IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMHB_V_X_1_G | I_0101_MGE_0102IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102IMHB_V_X_1_G | I | 0101 | MGE | 0102IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0102IMLO_A_X_1_mm_s | I_0101_MGE_0102IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102IMLO_A_X_1_mm_s | I | 0101 | MGE | 0102IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102IMLB_V_X_1_G | I_0101_MGE_0102IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102IMLB_V_X_1_G | I | 0101 | MGE | 0102IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0102IMAMP_K_X_1_ | I_0101_MGE_0102IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0102IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0102IMAMP_K_X_1_ | I | 0101 | MGE | 0102IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_S1Amp4_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0102LSGSGMF_A_X_1_mm_s | I_0101_MGE_0102LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0102LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSGSSER1_A_X_1_ | I_0101_MGE_0102LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102LSGSSER1_A_X_1_ | I | 0101 | MGE | 0102LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0102LSGSSER2_A_X_1_ | I_0101_MGE_0102LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0102LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0102LSGSSER2_A_X_1_ | I | 0101 | MGE | 0102LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_1_mm_s | I_0101_MGE_0102LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_1_mm_s | I_0101_MGE_0102LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_2_mm_s | I_0101_MGE_0102LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_2_mm_s | I_0101_MGE_0102LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_3_mm_s | I_0101_MGE_0102LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_3_mm_s | I_0101_MGE_0102LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_4_mm_s | I_0101_MGE_0102LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_4_mm_s | I_0101_MGE_0102LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_5_mm_s | I_0101_MGE_0102LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_5_mm_s | I_0101_MGE_0102LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0102LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0102LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0102LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0102LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRBSF_A_X_6_mm_s | I_0101_MGE_0102LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0102LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSBRFTF_A_X_6_mm_s | I_0101_MGE_0102LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0102LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSHB_V_X_1_G | I_0101_MGE_0102LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102LSHB_V_X_1_G | I | 0101 | MGE | 0102LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0102LSLO_A_X_1_mm_s | I_0101_MGE_0102LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSLO_A_X_1_mm_s | I | 0101 | MGE | 0102LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0102LSLB_V_X_1_G | I_0101_MGE_0102LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0102LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0102LSLB_V_X_1_G | I | 0101 | MGE | 0102LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0102LSAMP_K_X_1_ | I_0101_MGE_0102LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0102LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0102LSAMP_K_X_1_ | I | 0101 | MGE | 0102LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_S1Amp2_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0102LSUN_A_X_1_mm_s | I_0101_MGE_0102LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0102LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0102LSUN_A_X_1_mm_s | I | 0101 | MGE | 0102LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCHB_V_X_1_G | I_0101_MOT_0102MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0102MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0102MCHB_V_X_1_G | I | 0101 | MOT | 0102MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0102MCLO_A_X_1_mm_s | I_0101_MOT_0102MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCLO_A_X_1_mm_s | I | 0101 | MOT | 0102MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCLB_V_X_1_G | I_0101_MOT_0102MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0102MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0102MCLB_V_X_1_G | I | 0101 | MOT | 0102MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0102MCMA_A_X_1_mm_s | I_0101_MOT_0102MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCMA_A_X_1_mm_s | I | 0101 | MOT | 0102MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0102MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0102MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0102MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0102MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBSF_A_X_1_mm_s | I_0101_MOT_0102MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0102MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRFTF_A_X_1_mm_s | I_0101_MOT_0102MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0102MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0102MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0102MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0102MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0102MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRBSF_A_X_2_mm_s | I_0101_MOT_0102MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0102MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCBRFTF_A_X_2_mm_s | I_0101_MOT_0102MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0102MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCUN_A_X_1_mm_s | I_0101_MOT_0102MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MCUN_A_X_1_mm_s | I | 0101 | MOT | 0102MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MCAMP_K_X_1_ | I_0101_MOT_0102MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0102MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0102MCAMP_K_X_1_ | I | 0101 | MOT | 0102MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingsidet_S1Amp1_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MOT_0102MNHB_V_X_1_G | I_0101_MOT_0102MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0102MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0102MNHB_V_X_1_G | I | 0101 | MOT | 0102MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0102MNLO_A_X_1_mm_s | I_0101_MOT_0102MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNLO_A_X_1_mm_s | I | 0101 | MOT | 0102MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNLB_V_X_1_G | I_0101_MOT_0102MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0102MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0102MNLB_V_X_1_G | I | 0101 | MOT | 0102MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0102MNMA_A_X_1_mm_s | I_0101_MOT_0102MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNMA_A_X_1_mm_s | I | 0101 | MOT | 0102MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0102MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0102MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0102MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0102MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBSF_A_X_1_mm_s | I_0101_MOT_0102MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0102MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRFTF_A_X_1_mm_s | I_0101_MOT_0102MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0102MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0102MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0102MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0102MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0102MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRBSF_A_X_2_mm_s | I_0101_MOT_0102MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0102MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNBRFTF_A_X_2_mm_s | I_0101_MOT_0102MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0102MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0102MNAMP_K_X_1_ | I_0101_MOT_0102MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0102MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0102MNAMP_K_X_1_ | I | 0101 | MOT | 0102MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_S1Amp4_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MOT_0102MNUN_A_X_1_mm_s | I_0101_MOT_0102MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0102MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0102MNUN_A_X_1_mm_s | I | 0101 | MOT | 0102MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSGSGMF_A_X_1_mm_s | I_0101_MGE_0103HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0103HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSGSSER1_A_X_1_ | I_0101_MGE_0103HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103HSGSSER1_A_X_1_ | I | 0101 | MGE | 0103HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0103HSGSSER2_A_X_1_ | I_0101_MGE_0103HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103HSGSSER2_A_X_1_ | I | 0101 | MGE | 0103HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0103HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0103HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0103HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0103HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBSF_A_X_1_mm_s | I_0101_MGE_0103HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0103HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRFTF_A_X_1_mm_s | I_0101_MGE_0103HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0103HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0103HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0103HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0103HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0103HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBSF_A_X_2_mm_s | I_0101_MGE_0103HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0103HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRFTF_A_X_2_mm_s | I_0101_MGE_0103HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0103HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0103HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0103HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0103HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0103HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRBSF_A_X_3_mm_s | I_0101_MGE_0103HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0103HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSBRFTF_A_X_3_mm_s | I_0101_MGE_0103HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0103HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSHB_V_X_1_G | I_0101_MGE_0103HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103HSHB_V_X_1_G | I | 0101 | MGE | 0103HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0103HSLO_A_X_1_mm_s | I_0101_MGE_0103HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103HSLO_A_X_1_mm_s | I | 0101 | MGE | 0103HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103HSLB_V_X_1_G | I_0101_MGE_0103HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103HSLB_V_X_1_G | I | 0101 | MGE | 0103HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0103HSAMP_K_X_1_ | I_0101_MGE_0103HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0103HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0103HSAMP_K_X_1_ | I | 0101 | MGE | 0103HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_S1Amp2_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSGMF_A_X_1_mm_s | I_0101_MGE_0103IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0103IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSSER1_A_X_1_ | I_0101_MGE_0103IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103IMGSSER1_A_X_1_ | I | 0101 | MGE | 0103IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSSER2_A_X_1_ | I_0101_MGE_0103IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103IMGSSER2_A_X_1_ | I | 0101 | MGE | 0103IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSGMF_A_X_2_mm_s | I_0101_MGE_0103IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0103IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSSER1_A_X_2_ | I_0101_MGE_0103IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0103IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0103IMGSSER1_A_X_2_ | I | 0101 | MGE | 0103IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0103IMGSSER2_A_X_2_ | I_0101_MGE_0103IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0103IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0103IMGSSER2_A_X_2_ | I | 0101 | MGE | 0103IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0103IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0103IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0103IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0103IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBSF_A_X_1_mm_s | I_0101_MGE_0103IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0103IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRFTF_A_X_1_mm_s | I_0101_MGE_0103IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0103IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0103IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0103IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0103IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0103IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRBSF_A_X_2_mm_s | I_0101_MGE_0103IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0103IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMBRFTF_A_X_2_mm_s | I_0101_MGE_0103IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0103IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMHB_V_X_1_G | I_0101_MGE_0103IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103IMHB_V_X_1_G | I | 0101 | MGE | 0103IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0103IMLO_A_X_1_mm_s | I_0101_MGE_0103IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103IMLO_A_X_1_mm_s | I | 0101 | MGE | 0103IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103IMLB_V_X_1_G | I_0101_MGE_0103IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103IMLB_V_X_1_G | I | 0101 | MGE | 0103IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0103IMAMP_K_X_1_ | I_0101_MGE_0103IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0103IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0103IMAMP_K_X_1_ | I | 0101 | MGE | 0103IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_S1Amp4_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MGE_0103LSGSGMF_A_X_1_mm_s | I_0101_MGE_0103LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0103LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSGSSER1_A_X_1_ | I_0101_MGE_0103LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103LSGSSER1_A_X_1_ | I | 0101 | MGE | 0103LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0103LSGSSER2_A_X_1_ | I_0101_MGE_0103LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0103LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0103LSGSSER2_A_X_1_ | I | 0101 | MGE | 0103LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_1_mm_s | I_0101_MGE_0103LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_1_mm_s | I_0101_MGE_0103LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_2_mm_s | I_0101_MGE_0103LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_2_mm_s | I_0101_MGE_0103LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_3_mm_s | I_0101_MGE_0103LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_3_mm_s | I_0101_MGE_0103LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_4_mm_s | I_0101_MGE_0103LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_4_mm_s | I_0101_MGE_0103LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_5_mm_s | I_0101_MGE_0103LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_5_mm_s | I_0101_MGE_0103LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0103LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0103LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0103LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0103LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRBSF_A_X_6_mm_s | I_0101_MGE_0103LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0103LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSBRFTF_A_X_6_mm_s | I_0101_MGE_0103LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0103LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSHB_V_X_1_G | I_0101_MGE_0103LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103LSHB_V_X_1_G | I | 0101 | MGE | 0103LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0103LSLO_A_X_1_mm_s | I_0101_MGE_0103LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSLO_A_X_1_mm_s | I | 0101 | MGE | 0103LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0103LSLB_V_X_1_G | I_0101_MGE_0103LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0103LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0103LSLB_V_X_1_G | I | 0101 | MGE | 0103LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0103LSAMP_K_X_1_ | I_0101_MGE_0103LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0103LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0103LSAMP_K_X_1_ | I | 0101 | MGE | 0103LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_S1Amp3_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MGE_0103LSUN_A_X_1_mm_s | I_0101_MGE_0103LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0103LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0103LSUN_A_X_1_mm_s | I | 0101 | MGE | 0103LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCHB_V_X_1_G | I_0101_MOT_0103MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0103MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0103MCHB_V_X_1_G | I | 0101 | MOT | 0103MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0103MCLO_A_X_1_mm_s | I_0101_MOT_0103MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCLO_A_X_1_mm_s | I | 0101 | MOT | 0103MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCLB_V_X_1_G | I_0101_MOT_0103MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0103MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0103MCLB_V_X_1_G | I | 0101 | MOT | 0103MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0103MCMA_A_X_1_mm_s | I_0101_MOT_0103MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCMA_A_X_1_mm_s | I | 0101 | MOT | 0103MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0103MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0103MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0103MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0103MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBSF_A_X_1_mm_s | I_0101_MOT_0103MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0103MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRFTF_A_X_1_mm_s | I_0101_MOT_0103MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0103MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0103MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0103MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0103MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0103MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRBSF_A_X_2_mm_s | I_0101_MOT_0103MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0103MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCBRFTF_A_X_2_mm_s | I_0101_MOT_0103MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0103MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MCAMP_K_X_1_ | I_0101_MOT_0103MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0103MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0103MCAMP_K_X_1_ | I | 0101 | MOT | 0103MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_S1Amp2_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MOT_0103MCUN_A_X_1_mm_s | I_0101_MOT_0103MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MCUN_A_X_1_mm_s | I | 0101 | MOT | 0103MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNHB_V_X_1_G | I_0101_MOT_0103MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0103MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0103MNHB_V_X_1_G | I | 0101 | MOT | 0103MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0103MNLO_A_X_1_mm_s | I_0101_MOT_0103MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNLO_A_X_1_mm_s | I | 0101 | MOT | 0103MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNLB_V_X_1_G | I_0101_MOT_0103MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0103MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0103MNLB_V_X_1_G | I | 0101 | MOT | 0103MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0103MNMA_A_X_1_mm_s | I_0101_MOT_0103MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNMA_A_X_1_mm_s | I | 0101 | MOT | 0103MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0103MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0103MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0103MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0103MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBSF_A_X_1_mm_s | I_0101_MOT_0103MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0103MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRFTF_A_X_1_mm_s | I_0101_MOT_0103MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0103MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0103MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0103MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0103MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0103MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRBSF_A_X_2_mm_s | I_0101_MOT_0103MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0103MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNBRFTF_A_X_2_mm_s | I_0101_MOT_0103MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0103MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0103MNAMP_K_X_1_ | I_0101_MOT_0103MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0103MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0103MNAMP_K_X_1_ | I | 0101 | MOT | 0103MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_S1Amp4_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MOT_0103MNUN_A_X_1_mm_s | I_0101_MOT_0103MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0103MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0103MNUN_A_X_1_mm_s | I | 0101 | MOT | 0103MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSGSGMF_A_X_1_mm_s | I_0101_MGE_0201HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0201HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSGSSER1_A_X_1_ | I_0101_MGE_0201HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201HSGSSER1_A_X_1_ | I | 0101 | MGE | 0201HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0201HSGSSER2_A_X_1_ | I_0101_MGE_0201HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201HSGSSER2_A_X_1_ | I | 0101 | MGE | 0201HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0201HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0201HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0201HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0201HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBSF_A_X_1_mm_s | I_0101_MGE_0201HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0201HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRFTF_A_X_1_mm_s | I_0101_MGE_0201HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0201HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0201HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0201HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0201HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0201HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBSF_A_X_2_mm_s | I_0101_MGE_0201HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0201HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRFTF_A_X_2_mm_s | I_0101_MGE_0201HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0201HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0201HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0201HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0201HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0201HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRBSF_A_X_3_mm_s | I_0101_MGE_0201HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0201HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSBRFTF_A_X_3_mm_s | I_0101_MGE_0201HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0201HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSHB_V_X_1_G | I_0101_MGE_0201HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201HSHB_V_X_1_G | I | 0101 | MGE | 0201HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0201HSLO_A_X_1_mm_s | I_0101_MGE_0201HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201HSLO_A_X_1_mm_s | I | 0101 | MGE | 0201HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201HSLB_V_X_1_G | I_0101_MGE_0201HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201HSLB_V_X_1_G | I | 0101 | MGE | 0201HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0201HSAMP_K_X_1_ | I_0101_MGE_0201HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0201HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0201HSAMP_K_X_1_ | I | 0101 | MGE | 0201HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_S2Amp1_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSGMF_A_X_1_mm_s | I_0101_MGE_0201IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0201IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSSER1_A_X_1_ | I_0101_MGE_0201IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201IMGSSER1_A_X_1_ | I | 0101 | MGE | 0201IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSSER2_A_X_1_ | I_0101_MGE_0201IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201IMGSSER2_A_X_1_ | I | 0101 | MGE | 0201IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSGMF_A_X_2_mm_s | I_0101_MGE_0201IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0201IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSSER1_A_X_2_ | I_0101_MGE_0201IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0201IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0201IMGSSER1_A_X_2_ | I | 0101 | MGE | 0201IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0201IMGSSER2_A_X_2_ | I_0101_MGE_0201IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0201IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0201IMGSSER2_A_X_2_ | I | 0101 | MGE | 0201IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0201IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0201IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0201IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0201IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBSF_A_X_1_mm_s | I_0101_MGE_0201IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0201IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRFTF_A_X_1_mm_s | I_0101_MGE_0201IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0201IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0201IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0201IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0201IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0201IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRBSF_A_X_2_mm_s | I_0101_MGE_0201IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0201IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMBRFTF_A_X_2_mm_s | I_0101_MGE_0201IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0201IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMHB_V_X_1_G | I_0101_MGE_0201IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201IMHB_V_X_1_G | I | 0101 | MGE | 0201IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0201IMLO_A_X_1_mm_s | I_0101_MGE_0201IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201IMLO_A_X_1_mm_s | I | 0101 | MGE | 0201IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201IMLB_V_X_1_G | I_0101_MGE_0201IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201IMLB_V_X_1_G | I | 0101 | MGE | 0201IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0201IMAMP_K_X_1_ | I_0101_MGE_0201IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0201IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0201IMAMP_K_X_1_ | I | 0101 | MGE | 0201IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_S2Amp3_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MGE_0201LSGSGMF_A_X_1_mm_s | I_0101_MGE_0201LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0201LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSGSSER1_A_X_1_ | I_0101_MGE_0201LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201LSGSSER1_A_X_1_ | I | 0101 | MGE | 0201LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0201LSGSSER2_A_X_1_ | I_0101_MGE_0201LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0201LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0201LSGSSER2_A_X_1_ | I | 0101 | MGE | 0201LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_1_mm_s | I_0101_MGE_0201LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_1_mm_s | I_0101_MGE_0201LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_2_mm_s | I_0101_MGE_0201LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_2_mm_s | I_0101_MGE_0201LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_3_mm_s | I_0101_MGE_0201LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_3_mm_s | I_0101_MGE_0201LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_4_mm_s | I_0101_MGE_0201LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_4_mm_s | I_0101_MGE_0201LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_5_mm_s | I_0101_MGE_0201LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_5_mm_s | I_0101_MGE_0201LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0201LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0201LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0201LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0201LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRBSF_A_X_6_mm_s | I_0101_MGE_0201LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0201LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSBRFTF_A_X_6_mm_s | I_0101_MGE_0201LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0201LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSHB_V_X_1_G | I_0101_MGE_0201LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201LSHB_V_X_1_G | I | 0101 | MGE | 0201LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0201LSLO_A_X_1_mm_s | I_0101_MGE_0201LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSLO_A_X_1_mm_s | I | 0101 | MGE | 0201LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0201LSLB_V_X_1_G | I_0101_MGE_0201LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0201LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0201LSLB_V_X_1_G | I | 0101 | MGE | 0201LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0201LSAMP_K_X_1_ | I_0101_MGE_0201LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0201LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0201LSAMP_K_X_1_ | I | 0101 | MGE | 0201LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_S2Amp1_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MGE_0201LSUN_A_X_1_mm_s | I_0101_MGE_0201LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0201LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0201LSUN_A_X_1_mm_s | I | 0101 | MGE | 0201LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCHB_V_X_1_G | I_0101_MOT_0201MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0201MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0201MCHB_V_X_1_G | I | 0101 | MOT | 0201MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0201MCLO_A_X_1_mm_s | I_0101_MOT_0201MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCLO_A_X_1_mm_s | I | 0101 | MOT | 0201MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCLB_V_X_1_G | I_0101_MOT_0201MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0201MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0201MCLB_V_X_1_G | I | 0101 | MOT | 0201MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0201MCMA_A_X_1_mm_s | I_0101_MOT_0201MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCMA_A_X_1_mm_s | I | 0101 | MOT | 0201MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0201MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0201MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0201MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0201MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBSF_A_X_1_mm_s | I_0101_MOT_0201MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0201MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRFTF_A_X_1_mm_s | I_0101_MOT_0201MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0201MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0201MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0201MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0201MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0201MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRBSF_A_X_2_mm_s | I_0101_MOT_0201MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0201MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCBRFTF_A_X_2_mm_s | I_0101_MOT_0201MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0201MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MCAMP_K_X_1_ | I_0101_MOT_0201MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0201MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0201MCAMP_K_X_1_ | I | 0101 | MOT | 0201MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_S2Amp1_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MOT_0201MCUN_A_X_1_mm_s | I_0101_MOT_0201MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MCUN_A_X_1_mm_s | I | 0101 | MOT | 0201MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNHB_V_X_1_G | I_0101_MOT_0201MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0201MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0201MNHB_V_X_1_G | I | 0101 | MOT | 0201MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0201MNLO_A_X_1_mm_s | I_0101_MOT_0201MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNLO_A_X_1_mm_s | I | 0101 | MOT | 0201MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNLB_V_X_1_G | I_0101_MOT_0201MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0201MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0201MNLB_V_X_1_G | I | 0101 | MOT | 0201MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0201MNMA_A_X_1_mm_s | I_0101_MOT_0201MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNMA_A_X_1_mm_s | I | 0101 | MOT | 0201MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0201MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0201MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0201MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0201MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBSF_A_X_1_mm_s | I_0101_MOT_0201MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0201MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRFTF_A_X_1_mm_s | I_0101_MOT_0201MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0201MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0201MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0201MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0201MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0201MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRBSF_A_X_2_mm_s | I_0101_MOT_0201MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0201MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNBRFTF_A_X_2_mm_s | I_0101_MOT_0201MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0201MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0201MNAMP_K_X_1_ | I_0101_MOT_0201MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0201MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0201MNAMP_K_X_1_ | I | 0101 | MOT | 0201MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_S2Amp3_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MOT_0201MNUN_A_X_1_mm_s | I_0101_MOT_0201MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0201MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0201MNUN_A_X_1_mm_s | I | 0101 | MOT | 0201MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSGSGMF_A_X_1_mm_s | I_0101_MGE_0202HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0202HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSGSSER1_A_X_1_ | I_0101_MGE_0202HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202HSGSSER1_A_X_1_ | I | 0101 | MGE | 0202HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0202HSGSSER2_A_X_1_ | I_0101_MGE_0202HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202HSGSSER2_A_X_1_ | I | 0101 | MGE | 0202HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0202HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0202HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0202HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0202HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBSF_A_X_1_mm_s | I_0101_MGE_0202HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0202HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRFTF_A_X_1_mm_s | I_0101_MGE_0202HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0202HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0202HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0202HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0202HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0202HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBSF_A_X_2_mm_s | I_0101_MGE_0202HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0202HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRFTF_A_X_2_mm_s | I_0101_MGE_0202HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0202HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0202HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0202HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0202HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0202HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRBSF_A_X_3_mm_s | I_0101_MGE_0202HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0202HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSBRFTF_A_X_3_mm_s | I_0101_MGE_0202HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0202HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSHB_V_X_1_G | I_0101_MGE_0202HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202HSHB_V_X_1_G | I | 0101 | MGE | 0202HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0202HSLO_A_X_1_mm_s | I_0101_MGE_0202HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202HSLO_A_X_1_mm_s | I | 0101 | MGE | 0202HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202HSLB_V_X_1_G | I_0101_MGE_0202HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202HSLB_V_X_1_G | I | 0101 | MGE | 0202HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0202HSAMP_K_X_1_ | I_0101_MGE_0202HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0202HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0202HSAMP_K_X_1_ | I | 0101 | MGE | 0202HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_S2Amp2_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSGMF_A_X_1_mm_s | I_0101_MGE_0202IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0202IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSSER1_A_X_1_ | I_0101_MGE_0202IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202IMGSSER1_A_X_1_ | I | 0101 | MGE | 0202IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSSER2_A_X_1_ | I_0101_MGE_0202IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202IMGSSER2_A_X_1_ | I | 0101 | MGE | 0202IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSGMF_A_X_2_mm_s | I_0101_MGE_0202IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0202IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSSER1_A_X_2_ | I_0101_MGE_0202IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0202IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0202IMGSSER1_A_X_2_ | I | 0101 | MGE | 0202IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0202IMGSSER2_A_X_2_ | I_0101_MGE_0202IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0202IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0202IMGSSER2_A_X_2_ | I | 0101 | MGE | 0202IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0202IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0202IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0202IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0202IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBSF_A_X_1_mm_s | I_0101_MGE_0202IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0202IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRFTF_A_X_1_mm_s | I_0101_MGE_0202IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0202IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0202IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0202IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0202IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0202IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRBSF_A_X_2_mm_s | I_0101_MGE_0202IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0202IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMBRFTF_A_X_2_mm_s | I_0101_MGE_0202IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0202IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMHB_V_X_1_G | I_0101_MGE_0202IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202IMHB_V_X_1_G | I | 0101 | MGE | 0202IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0202IMLO_A_X_1_mm_s | I_0101_MGE_0202IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202IMLO_A_X_1_mm_s | I | 0101 | MGE | 0202IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202IMLB_V_X_1_G | I_0101_MGE_0202IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202IMLB_V_X_1_G | I | 0101 | MGE | 0202IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0202IMAMP_K_X_1_ | I_0101_MGE_0202IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0202IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0202IMAMP_K_X_1_ | I | 0101 | MGE | 0202IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_S2Amp4_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0202LSGSGMF_A_X_1_mm_s | I_0101_MGE_0202LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0202LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSGSSER1_A_X_1_ | I_0101_MGE_0202LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202LSGSSER1_A_X_1_ | I | 0101 | MGE | 0202LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0202LSGSSER2_A_X_1_ | I_0101_MGE_0202LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0202LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0202LSGSSER2_A_X_1_ | I | 0101 | MGE | 0202LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_1_mm_s | I_0101_MGE_0202LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_1_mm_s | I_0101_MGE_0202LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_2_mm_s | I_0101_MGE_0202LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_2_mm_s | I_0101_MGE_0202LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_3_mm_s | I_0101_MGE_0202LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_3_mm_s | I_0101_MGE_0202LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_4_mm_s | I_0101_MGE_0202LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_4_mm_s | I_0101_MGE_0202LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_5_mm_s | I_0101_MGE_0202LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_5_mm_s | I_0101_MGE_0202LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0202LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0202LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0202LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0202LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRBSF_A_X_6_mm_s | I_0101_MGE_0202LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0202LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSBRFTF_A_X_6_mm_s | I_0101_MGE_0202LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0202LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSHB_V_X_1_G | I_0101_MGE_0202LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202LSHB_V_X_1_G | I | 0101 | MGE | 0202LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0202LSLO_A_X_1_mm_s | I_0101_MGE_0202LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSLO_A_X_1_mm_s | I | 0101 | MGE | 0202LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0202LSLB_V_X_1_G | I_0101_MGE_0202LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0202LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0202LSLB_V_X_1_G | I | 0101 | MGE | 0202LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0202LSAMP_K_X_1_ | I_0101_MGE_0202LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0202LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0202LSAMP_K_X_1_ | I | 0101 | MGE | 0202LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_S2Amp2_Ch2Status |  |  | Y | N
BE-PSG_I_0101_MGE_0202LSUN_A_X_1_mm_s | I_0101_MGE_0202LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0202LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0202LSUN_A_X_1_mm_s | I | 0101 | MGE | 0202LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCHB_V_X_1_G | I_0101_MOT_0202MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0202MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0202MCHB_V_X_1_G | I | 0101 | MOT | 0202MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0202MCLO_A_X_1_mm_s | I_0101_MOT_0202MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCLO_A_X_1_mm_s | I | 0101 | MOT | 0202MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCLB_V_X_1_G | I_0101_MOT_0202MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0202MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0202MCLB_V_X_1_G | I | 0101 | MOT | 0202MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0202MCMA_A_X_1_mm_s | I_0101_MOT_0202MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCMA_A_X_1_mm_s | I | 0101 | MOT | 0202MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0202MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0202MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0202MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0202MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBSF_A_X_1_mm_s | I_0101_MOT_0202MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0202MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRFTF_A_X_1_mm_s | I_0101_MOT_0202MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0202MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0202MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0202MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0202MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0202MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRBSF_A_X_2_mm_s | I_0101_MOT_0202MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0202MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCBRFTF_A_X_2_mm_s | I_0101_MOT_0202MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0202MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MCAMP_K_X_1_ | I_0101_MOT_0202MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0202MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0202MCAMP_K_X_1_ | I | 0101 | MOT | 0202MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_S2Amp1_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MOT_0202MCUN_A_X_1_mm_s | I_0101_MOT_0202MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MCUN_A_X_1_mm_s | I | 0101 | MOT | 0202MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNHB_V_X_1_G | I_0101_MOT_0202MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0202MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0202MNHB_V_X_1_G | I | 0101 | MOT | 0202MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0202MNLO_A_X_1_mm_s | I_0101_MOT_0202MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNLO_A_X_1_mm_s | I | 0101 | MOT | 0202MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNLB_V_X_1_G | I_0101_MOT_0202MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0202MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0202MNLB_V_X_1_G | I | 0101 | MOT | 0202MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0202MNMA_A_X_1_mm_s | I_0101_MOT_0202MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNMA_A_X_1_mm_s | I | 0101 | MOT | 0202MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0202MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0202MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0202MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0202MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBSF_A_X_1_mm_s | I_0101_MOT_0202MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0202MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRFTF_A_X_1_mm_s | I_0101_MOT_0202MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0202MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0202MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0202MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0202MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0202MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRBSF_A_X_2_mm_s | I_0101_MOT_0202MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0202MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNBRFTF_A_X_2_mm_s | I_0101_MOT_0202MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0202MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0202MNAMP_K_X_1_ | I_0101_MOT_0202MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0202MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0202MNAMP_K_X_1_ | I | 0101 | MOT | 0202MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_S2Amp4_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MOT_0202MNUN_A_X_1_mm_s | I_0101_MOT_0202MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0202MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0202MNUN_A_X_1_mm_s | I | 0101 | MOT | 0202MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSGSGMF_A_X_1_mm_s | I_0101_MGE_0203HSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0203HSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSGSSER1_A_X_1_ | I_0101_MGE_0203HSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203HSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203HSGSSER1_A_X_1_ | I | 0101 | MGE | 0203HSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0203HSGSSER2_A_X_1_ | I_0101_MGE_0203HSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203HSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203HSGSSER2_A_X_1_ | I | 0101 | MGE | 0203HSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFI_A_X_1_mm_s | I_0101_MGE_0203HSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0203HSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFO_A_X_1_mm_s | I_0101_MGE_0203HSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0203HSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBSF_A_X_1_mm_s | I_0101_MGE_0203HSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0203HSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRFTF_A_X_1_mm_s | I_0101_MGE_0203HSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0203HSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFI_A_X_2_mm_s | I_0101_MGE_0203HSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0203HSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFO_A_X_2_mm_s | I_0101_MGE_0203HSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0203HSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBSF_A_X_2_mm_s | I_0101_MGE_0203HSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0203HSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRFTF_A_X_2_mm_s | I_0101_MGE_0203HSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0203HSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFI_A_X_3_mm_s | I_0101_MGE_0203HSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0203HSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBPFO_A_X_3_mm_s | I_0101_MGE_0203HSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0203HSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRBSF_A_X_3_mm_s | I_0101_MGE_0203HSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0203HSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSBRFTF_A_X_3_mm_s | I_0101_MGE_0203HSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0203HSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSHB_V_X_1_G | I_0101_MGE_0203HSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203HSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203HSHB_V_X_1_G | I | 0101 | MGE | 0203HSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0203HSLO_A_X_1_mm_s | I_0101_MGE_0203HSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203HSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203HSLO_A_X_1_mm_s | I | 0101 | MGE | 0203HSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203HSLB_V_X_1_G | I_0101_MGE_0203HSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203HSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203HSLB_V_X_1_G | I | 0101 | MGE | 0203HSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0203HSAMP_K_X_1_ | I_0101_MGE_0203HSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0203HSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0203HSAMP_K_X_1_ | I | 0101 | MGE | 0203HSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_S2Amp2_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSGMF_A_X_1_mm_s | I_0101_MGE_0203IMGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0203IMGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSSER1_A_X_1_ | I_0101_MGE_0203IMGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203IMGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203IMGSSER1_A_X_1_ | I | 0101 | MGE | 0203IMGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSSER2_A_X_1_ | I_0101_MGE_0203IMGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203IMGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203IMGSSER2_A_X_1_ | I | 0101 | MGE | 0203IMGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSGMF_A_X_2_mm_s | I_0101_MGE_0203IMGSGMF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMGSGMF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMGSGMF_A_X_2_mm_s | I | 0101 | MGE | 0203IMGSGMF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSSER1_A_X_2_ | I_0101_MGE_0203IMGSSER1_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0203IMGSSER1_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0203IMGSSER1_A_X_2_ | I | 0101 | MGE | 0203IMGSSER1 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0203IMGSSER2_A_X_2_ | I_0101_MGE_0203IMGSSER2_A_X_2_ | BE-PSG_I_0101_MGE | MGE_0203IMGSSER2_A_X_2_ | BE-PSG | TRA | I_0101_MGE_0203IMGSSER2_A_X_2_ | I | 0101 | MGE | 0203IMGSSER2 | A | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBPFI_A_X_1_mm_s | I_0101_MGE_0203IMBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0203IMBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBPFO_A_X_1_mm_s | I_0101_MGE_0203IMBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0203IMBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBSF_A_X_1_mm_s | I_0101_MGE_0203IMBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0203IMBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRFTF_A_X_1_mm_s | I_0101_MGE_0203IMBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0203IMBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBPFI_A_X_2_mm_s | I_0101_MGE_0203IMBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0203IMBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBPFO_A_X_2_mm_s | I_0101_MGE_0203IMBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0203IMBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRBSF_A_X_2_mm_s | I_0101_MGE_0203IMBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0203IMBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMBRFTF_A_X_2_mm_s | I_0101_MGE_0203IMBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0203IMBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMHB_V_X_1_G | I_0101_MGE_0203IMHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203IMHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203IMHB_V_X_1_G | I | 0101 | MGE | 0203IMHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0203IMLO_A_X_1_mm_s | I_0101_MGE_0203IMLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203IMLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203IMLO_A_X_1_mm_s | I | 0101 | MGE | 0203IMLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_LOOSNESS_IM_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203IMLB_V_X_1_G | I_0101_MGE_0203IMLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203IMLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203IMLB_V_X_1_G | I | 0101 | MGE | 0203IMLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0203IMAMP_K_X_1_ | I_0101_MGE_0203IMAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0203IMAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0203IMAMP_K_X_1_ | I | 0101 | MGE | 0203IMAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_S2Amp4_Ch4Status |  |  | Y | N
BE-PSG_I_0101_MGE_0203LSGSGMF_A_X_1_mm_s | I_0101_MGE_0203LSGSGMF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSGSGMF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSGSGMF_A_X_1_mm_s | I | 0101 | MGE | 0203LSGSGMF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSGSSER1_A_X_1_ | I_0101_MGE_0203LSGSSER1_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203LSGSSER1_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203LSGSSER1_A_X_1_ | I | 0101 | MGE | 0203LSGSSER1 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 |  |  | Y | N
BE-PSG_I_0101_MGE_0203LSGSSER2_A_X_1_ | I_0101_MGE_0203LSGSSER2_A_X_1_ | BE-PSG_I_0101_MGE | MGE_0203LSGSSER2_A_X_1_ | BE-PSG | TRA | I_0101_MGE_0203LSGSSER2_A_X_1_ | I | 0101 | MGE | 0203LSGSSER2 | A | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 |  |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_1_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_1_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_1_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_1_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_1_mm_s | I_0101_MGE_0203LSBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_1_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_1_mm_s | I_0101_MGE_0203LSBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_1_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_2_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_2_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_2_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_2_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_2_mm_s | I_0101_MGE_0203LSBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_2_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_2_mm_s | I_0101_MGE_0203LSBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_2_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_2_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_3_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_3_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_3_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_3_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_3_mm_s | I_0101_MGE_0203LSBRBSF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_3_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_3_mm_s | I_0101_MGE_0203LSBRFTF_A_X_3_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_3_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_3_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 3 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_4_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_4_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_4_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_4_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_4_mm_s | I_0101_MGE_0203LSBRBSF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_4_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_4_mm_s | I_0101_MGE_0203LSBRFTF_A_X_4_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_4_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_4_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 4 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_5_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_5_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_5_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_5_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_5_mm_s | I_0101_MGE_0203LSBRBSF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_5_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_5_mm_s | I_0101_MGE_0203LSBRFTF_A_X_5_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_5_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_5_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 5 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFI_A_X_6_mm_s | I_0101_MGE_0203LSBRBPFI_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFI_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFI_A_X_6_mm_s | I | 0101 | MGE | 0203LSBRBPFI | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBPFO_A_X_6_mm_s | I_0101_MGE_0203LSBRBPFO_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBPFO_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBPFO_A_X_6_mm_s | I | 0101 | MGE | 0203LSBRBPFO | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRBSF_A_X_6_mm_s | I_0101_MGE_0203LSBRBSF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRBSF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRBSF_A_X_6_mm_s | I | 0101 | MGE | 0203LSBRBSF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSBRFTF_A_X_6_mm_s | I_0101_MGE_0203LSBRFTF_A_X_6_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSBRFTF_A_X_6_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSBRFTF_A_X_6_mm_s | I | 0101 | MGE | 0203LSBRFTF | A | X | 6 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSHB_V_X_1_G | I_0101_MGE_0203LSHB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203LSHB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203LSHB_V_X_1_G | I | 0101 | MGE | 0203LSHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_Highband | G |  | Y | N
BE-PSG_I_0101_MGE_0203LSLO_A_X_1_mm_s | I_0101_MGE_0203LSLO_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSLO_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSLO_A_X_1_mm_s | I | 0101 | MGE | 0203LSLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_LOOSNESS_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MGE_0203LSLB_V_X_1_G | I_0101_MGE_0203LSLB_V_X_1_G | BE-PSG_I_0101_MGE | MGE_0203LSLB_V_X_1_G | BE-PSG | TRA | I_0101_MGE_0203LSLB_V_X_1_G | I | 0101 | MGE | 0203LSLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_Lowband | G |  | Y | N
BE-PSG_I_0101_MGE_0203LSAMP_K_X_1_ | I_0101_MGE_0203LSAMP_K_X_1_ | BE-PSG_I_0101_MGE | MGE_0203LSAMP_K_X_1_ | BE-PSG | TRA | I_0101_MGE_0203LSAMP_K_X_1_ | I | 0101 | MGE | 0203LSAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_S2Amp3_Ch1Status |  |  | Y | N
BE-PSG_I_0101_MGE_0203LSUN_A_X_1_mm_s | I_0101_MGE_0203LSUN_A_X_1_mm_s | BE-PSG_I_0101_MGE | MGE_0203LSUN_A_X_1_mm_s | BE-PSG | TRA | I_0101_MGE_0203LSUN_A_X_1_mm_s | I | 0101 | MGE | 0203LSUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_UNBALANCE_LS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCHB_V_X_1_G | I_0101_MOT_0203MCHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0203MCHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0203MCHB_V_X_1_G | I | 0101 | MOT | 0203MCHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0203MCLO_A_X_1_mm_s | I_0101_MOT_0203MCLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCLO_A_X_1_mm_s | I | 0101 | MOT | 0203MCLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCLB_V_X_1_G | I_0101_MOT_0203MCLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0203MCLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0203MCLB_V_X_1_G | I | 0101 | MOT | 0203MCLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0203MCMA_A_X_1_mm_s | I_0101_MOT_0203MCMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCMA_A_X_1_mm_s | I | 0101 | MOT | 0203MCMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBPFI_A_X_1_mm_s | I_0101_MOT_0203MCBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0203MCBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBPFO_A_X_1_mm_s | I_0101_MOT_0203MCBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0203MCBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBSF_A_X_1_mm_s | I_0101_MOT_0203MCBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0203MCBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRFTF_A_X_1_mm_s | I_0101_MOT_0203MCBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0203MCBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBPFI_A_X_2_mm_s | I_0101_MOT_0203MCBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0203MCBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBPFO_A_X_2_mm_s | I_0101_MOT_0203MCBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0203MCBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRBSF_A_X_2_mm_s | I_0101_MOT_0203MCBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0203MCBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCBRFTF_A_X_2_mm_s | I_0101_MOT_0203MCBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0203MCBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MCAMP_K_X_1_ | I_0101_MOT_0203MCAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0203MCAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0203MCAMP_K_X_1_ | I | 0101 | MOT | 0203MCAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_S2Amp2_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MOT_0203MCUN_A_X_1_mm_s | I_0101_MOT_0203MCUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MCUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MCUN_A_X_1_mm_s | I | 0101 | MOT | 0203MCUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNHB_V_X_1_G | I_0101_MOT_0203MNHB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0203MNHB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0203MNHB_V_X_1_G | I | 0101 | MOT | 0203MNHB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_Highband | G |  | Y | N
BE-PSG_I_0101_MOT_0203MNLO_A_X_1_mm_s | I_0101_MOT_0203MNLO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNLO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNLO_A_X_1_mm_s | I | 0101 | MOT | 0203MNLO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_LOOSNESS_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNLB_V_X_1_G | I_0101_MOT_0203MNLB_V_X_1_G | BE-PSG_I_0101_MOT | MOT_0203MNLB_V_X_1_G | BE-PSG | MOT | I_0101_MOT_0203MNLB_V_X_1_G | I | 0101 | MOT | 0203MNLB | V | X | 1 | G |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_Lowband | G |  | Y | N
BE-PSG_I_0101_MOT_0203MNMA_A_X_1_mm_s | I_0101_MOT_0203MNMA_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNMA_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNMA_A_X_1_mm_s | I | 0101 | MOT | 0203MNMA | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBPFI_A_X_1_mm_s | I_0101_MOT_0203MNBRBPFI_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBPFI_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBPFI_A_X_1_mm_s | I | 0101 | MOT | 0203MNBRBPFI | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBPFO_A_X_1_mm_s | I_0101_MOT_0203MNBRBPFO_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBPFO_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBPFO_A_X_1_mm_s | I | 0101 | MOT | 0203MNBRBPFO | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBSF_A_X_1_mm_s | I_0101_MOT_0203MNBRBSF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBSF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBSF_A_X_1_mm_s | I | 0101 | MOT | 0203MNBRBSF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRFTF_A_X_1_mm_s | I_0101_MOT_0203MNBRFTF_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRFTF_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRFTF_A_X_1_mm_s | I | 0101 | MOT | 0203MNBRFTF | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBPFI_A_X_2_mm_s | I_0101_MOT_0203MNBRBPFI_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBPFI_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBPFI_A_X_2_mm_s | I | 0101 | MOT | 0203MNBRBPFI | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBPFO_A_X_2_mm_s | I_0101_MOT_0203MNBRBPFO_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBPFO_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBPFO_A_X_2_mm_s | I | 0101 | MOT | 0203MNBRBPFO | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRBSF_A_X_2_mm_s | I_0101_MOT_0203MNBRBSF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRBSF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRBSF_A_X_2_mm_s | I | 0101 | MOT | 0203MNBRBSF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNBRFTF_A_X_2_mm_s | I_0101_MOT_0203MNBRFTF_A_X_2_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNBRFTF_A_X_2_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNBRFTF_A_X_2_mm_s | I | 0101 | MOT | 0203MNBRFTF | A | X | 2 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | mm_s |  | Y | N
BE-PSG_I_0101_MOT_0203MNAMP_K_X_1_ | I_0101_MOT_0203MNAMP_K_X_1_ | BE-PSG_I_0101_MOT | MOT_0203MNAMP_K_X_1_ | BE-PSG | MOT | I_0101_MOT_0203MNAMP_K_X_1_ | I | 0101 | MOT | 0203MNAMP | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_S2Amp4_Ch3Status |  |  | Y | N
BE-PSG_I_0101_MOT_0203MNUN_A_X_1_mm_s | I_0101_MOT_0203MNUN_A_X_1_mm_s | BE-PSG_I_0101_MOT | MOT_0203MNUN_A_X_1_mm_s | BE-PSG | MOT | I_0101_MOT_0203MNUN_A_X_1_mm_s | I | 0101 | MOT | 0203MNUN | A | X | 1 | mm_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_UNBALANCE_HS_SHAFT | mm_s |  | Y | N
BE-PSG_I_0101_AMP_0101DBAMP_X_X_1_ | I_0101_AMP_0101DBAMP_X_X_1_ | BE-PSG_I_0101_AMP | AMP_0101DBAMP_X_X_1_ | BE-PSG | AMP | I_0101_AMP_0101DBAMP_X_X_1_ | I | 0101 | AMP | 0101DBAMP | X | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP1_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0102DBAMP_X_X_1_ | I_0101_AMP_0102DBAMP_X_X_1_ | BE-PSG_I_0101_AMP | AMP_0102DBAMP_X_X_1_ | BE-PSG | AMP | I_0101_AMP_0102DBAMP_X_X_1_ | I | 0101 | AMP | 0102DBAMP | X | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP1_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0102DBAMP_X_X_2_ | I_0101_AMP_0102DBAMP_X_X_2_ | BE-PSG_I_0101_AMP | AMP_0102DBAMP_X_X_2_ | BE-PSG | AMP | I_0101_AMP_0102DBAMP_X_X_2_ | I | 0101 | AMP | 0102DBAMP | X | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP2_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0103DBAMP_X_X_2_ | I_0101_AMP_0103DBAMP_X_X_2_ | BE-PSG_I_0101_AMP | AMP_0103DBAMP_X_X_2_ | BE-PSG | AMP | I_0101_AMP_0103DBAMP_X_X_2_ | I | 0101 | AMP | 0103DBAMP | X | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP2_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0103DBAMP_X_X_3_ | I_0101_AMP_0103DBAMP_X_X_3_ | BE-PSG_I_0101_AMP | AMP_0103DBAMP_X_X_3_ | BE-PSG | AMP | I_0101_AMP_0103DBAMP_X_X_3_ | I | 0101 | AMP | 0103DBAMP | X | X | 3 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP3_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0101DBAMP_X_X_3_ | I_0101_AMP_0101DBAMP_X_X_3_ | BE-PSG_I_0101_AMP | AMP_0101DBAMP_X_X_3_ | BE-PSG | AMP | I_0101_AMP_0101DBAMP_X_X_3_ | I | 0101 | AMP | 0101DBAMP | X | X | 3 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP3_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0102DBAMP_X_X_4_ | I_0101_AMP_0102DBAMP_X_X_4_ | BE-PSG_I_0101_AMP | AMP_0102DBAMP_X_X_4_ | BE-PSG | AMP | I_0101_AMP_0102DBAMP_X_X_4_ | I | 0101 | AMP | 0102DBAMP | X | X | 4 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP4_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0103DBAMP_X_X_4_ | I_0101_AMP_0103DBAMP_X_X_4_ | BE-PSG_I_0101_AMP | AMP_0103DBAMP_X_X_4_ | BE-PSG | AMP | I_0101_AMP_0103DBAMP_X_X_4_ | I | 0101 | AMP | 0103DBAMP | X | X | 4 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP4_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0201DBAMP_X_X_1_ | I_0101_AMP_0201DBAMP_X_X_1_ | BE-PSG_I_0101_AMP | AMP_0201DBAMP_X_X_1_ | BE-PSG | AMP | I_0101_AMP_0201DBAMP_X_X_1_ | I | 0101 | AMP | 0201DBAMP | X | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP1_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0202DBAMP_X_X_1_ | I_0101_AMP_0202DBAMP_X_X_1_ | BE-PSG_I_0101_AMP | AMP_0202DBAMP_X_X_1_ | BE-PSG | AMP | I_0101_AMP_0202DBAMP_X_X_1_ | I | 0101 | AMP | 0202DBAMP | X | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP1_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0202DBAMP_X_X_2_ | I_0101_AMP_0202DBAMP_X_X_2_ | BE-PSG_I_0101_AMP | AMP_0202DBAMP_X_X_2_ | BE-PSG | AMP | I_0101_AMP_0202DBAMP_X_X_2_ | I | 0101 | AMP | 0202DBAMP | X | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP2_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0203DBAMP_X_X_2_ | I_0101_AMP_0203DBAMP_X_X_2_ | BE-PSG_I_0101_AMP | AMP_0203DBAMP_X_X_2_ | BE-PSG | AMP | I_0101_AMP_0203DBAMP_X_X_2_ | I | 0101 | AMP | 0203DBAMP | X | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP2_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0203DBAMP_X_X_3_ | I_0101_AMP_0203DBAMP_X_X_3_ | BE-PSG_I_0101_AMP | AMP_0203DBAMP_X_X_3_ | BE-PSG | AMP | I_0101_AMP_0203DBAMP_X_X_3_ | I | 0101 | AMP | 0203DBAMP | X | X | 3 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP3_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0201DBAMP_X_X_3_ | I_0101_AMP_0201DBAMP_X_X_3_ | BE-PSG_I_0101_AMP | AMP_0201DBAMP_X_X_3_ | BE-PSG | AMP | I_0101_AMP_0201DBAMP_X_X_3_ | I | 0101 | AMP | 0201DBAMP | X | X | 3 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP3_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0202DBAMP_X_X_4_ | I_0101_AMP_0202DBAMP_X_X_4_ | BE-PSG_I_0101_AMP | AMP_0202DBAMP_X_X_4_ | BE-PSG | AMP | I_0101_AMP_0202DBAMP_X_X_4_ | I | 0101 | AMP | 0202DBAMP | X | X | 4 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP4_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_0203DBAMP_X_X_4_ | I_0101_AMP_0203DBAMP_X_X_4_ | BE-PSG_I_0101_AMP | AMP_0203DBAMP_X_X_4_ | BE-PSG | AMP | I_0101_AMP_0203DBAMP_X_X_4_ | I | 0101 | AMP | 0203DBAMP | X | X | 4 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP4_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_AMP_NAMP_X_X_1_ | I_0101_AMP_NAMP_X_X_1_ | BE-PSG_I_0101_AMP | AMP_NAMP_X_X_1_ | BE-PSG | AMP | I_0101_AMP_NAMP_X_X_1_ | I | 0101 | AMP | NAMP | X | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_Wind_DeviceBattery |  |  | Y | N
BE-PSG_I_0101_NTR_N_D_X_1_Deg | I_0101_NTR_N_D_X_1_Deg | BE-PSG_I_0101_NTR | NTR_N_D_X_1_Deg | BE-PSG |  | I_0101_NTR_N_D_X_1_Deg | I | 0101 | NTR | N | D | X | 1 | Deg |  | SPX_DC_ENGIE_SAINTGHISLAIN_Wind_Winddirection | Deg |  | Y | N
BE-PSG_I_0101_NTR_N_S_X_1_m_s | I_0101_NTR_N_S_X_1_m_s | BE-PSG_I_0101_NTR | NTR_N_S_X_1_m_s | BE-PSG |  | I_0101_NTR_N_S_X_1_m_s | I | 0101 | NTR | N | S | X | 1 | m_s |  | SPX_DC_ENGIE_SAINTGHISLAIN_Wind_Windspeed | m_s |  | Y | Y
BE-PSG_I_0101_NTR_N_K_X_1_ | I_0101_NTR_N_K_X_1_ | BE-PSG_I_0101_NTR | NTR_N_K_X_1_ | BE-PSG |  | I_0101_NTR_N_K_X_1_ | I | 0101 | NTR | N | K | X | 1 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_WindDirection_Ch2Status |  |  | Y | N
BE-PSG_I_0101_NTR_N_K_X_2_ | I_0101_NTR_N_K_X_2_ | BE-PSG_I_0101_NTR | NTR_N_K_X_2_ | BE-PSG |  | I_0101_NTR_N_K_X_2_ | I | 0101 | NTR | N | K | X | 2 |  |  | SPX_DC_ENGIE_SAINTGHISLAIN_WindSpeed_Ch1Status |  |  | Y | N

## TAG_SOURCES
loc_code | tag_source_code | tag_source_type | tag_source_name | first_measure_dttm
BE-PSG | D | PI | PI_ENG | 2007-01-01
BE-PSG | I | LIB | ICARE_ENG | 2018-10-01

## TAG_FIRST_VALUES
tag_id | first_dttm | first_value
BE-PSG-01-BAA10-CE301P-X1V | 2012-07-17 10:43 | 340.9485
BE-PSG-01-MAJ11-CT501-X1V | 2007-10-01 | 28.28
BE-PSG-01-MAJ11-CT502-X1V | 2007-10-01 | 30.15
BE-PSG-01-MAJ12-CT501-X1V | 2007-10-01 | 30.62
BE-PSG-01-MAJ12-CT502-X1V | 2007-10-01 | 31.09
BE-PSG-01-MAJ13-CT501-X1V | 2007-10-01 | 29.92
BE-PSG-01-MAJ13-CT502-X1V | 2007-10-01 | 30.15
BE-PSG-01-MAJ14-CT501-X1V | 2007-10-01 | 30.62
BE-PSG-01-MAJ14-CT502-X1V | 2007-10-01 | 31.32
BE-PSG-01-MAJ15-AA101M-XS0 | 2015-06-09 18:04 | 1
BE-PSG-01-MAJ15-AA101M-XS8 | 2015-06-09 18:04 | 0
BE-PSG-01-MAJ21-AP010-XA0 | 2008-05-22 02:25
BE-PSG-01-MAJ21-AP010-XA1 | 2008-05-22 02:25 | 0
BE-PSG-01-MAJ21-AP020-XA0 | 2008-05-22 02:25
BE-PSG-01-MAJ21-CT501-X1V | 2007-10-01 | 18.75
BE-PSG-01-MAJ22-AP010-XA0 | 2008-05-22 02:25 | 0
BE-PSG-01-MAJ22-AP010-XA1 | 2008-05-22 02:25
BE-PSG-01-MAJ22-AP020-XA0 | 2008-05-22 02:25 | 0
BE-PSG-01-MAJ22-AP020-XA1 | 2008-05-22 02:25
BE-PSG-01-MAJ22-CT501-X1V | 2007-10-01 | 21.09
BE-PSG-01-MAJ30-AA100M-XS0 | 2015-06-09 18:04 | 1
BE-PSG-01-MAJ30-AA100M-XS8 | 2015-06-09 18:04 | 0
BE-PSG-01-MAJ32-CG100A-XS0 | 2015-06-09 18:04 | 1
BE-PSG-01-MAJ32-CG100B-XS8 | 2015-06-09 18:04 | 0
BE-PSG-01-MAJ32-CT501-X1V | 2015-06-09 10:29 | 53.1266
BE-PSG-01-MAJ33-AA100M-XS0 | 2015-06-09 18:04 | 1
BE-PSG-01-MAJ33-AA100M-XS8 | 2015-06-09 18:04 | 0
BE-PSG-01-MAJ61-CT501-X1V | 2007-10-01 | 19.68
BE-PSG-01-MAJ82-CT501-X1V | 2007-10-01 | 20.78
BE-PSG-01-MAG00-DP002-XH2 | 2008-06-04 23:17 | 0
BE-PSG-01-MAG00-EU906-X5V | 2007-10-01 | 64.14
BE-PSG-01-MAG10 | 2009-11-06 10:37 | 2
BE-PSG-01-MAG10-AN011-XA0 | 2008-05-22 07:52 | 0
BE-PSG-01-MAG10-AN011-XA1 | 2008-05-22 07:52
BE-PSG-01-MAG10-AN012-XA0 | 2008-05-20 07:22 | 0
BE-PSG-01-MAG10-AN012-XA1 | 2008-05-20 07:22
BE-PSG-01-MAG10-AN013-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN013-XA1 | 2008-05-17 14:35
BE-PSG-01-MAG10-AN014-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN014-XA1 | 2008-05-17 14:36
BE-PSG-01-MAG10-AN015-XA0 | 2008-05-21 09:28 | 0
BE-PSG-01-MAG10-AN015-XA1 | 2008-05-21 09:28
BE-PSG-01-MAG10-AN016-XA0 | 2008-05-22 10:45 | 0
BE-PSG-01-MAG10-AN016-XA1 | 2008-05-22 10:45
BE-PSG-01-MAG10-AN021-XA0 | 2008-05-22 07:00 | 0
BE-PSG-01-MAG10-AN021-XA1 | 2008-05-22 07:01
BE-PSG-01-MAG10-AN022-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN022-XA1 | 2008-05-17 14:36
BE-PSG-01-MAG10-AN023-XA0 | 2008-05-17 14:16 | 0
BE-PSG-01-MAG10-AN023-XA1 | 2008-05-17 14:16
BE-PSG-01-MAG10-AN024-XA0 | 2008-05-17 14:16 | 0
BE-PSG-01-MAG10-AN024-XA1 | 2008-05-17 14:16
BE-PSG-01-MAG10-AN025-XA0 | 2008-05-20 07:32 | 0
BE-PSG-01-MAG10-AN025-XA1 | 2008-05-20 07:32
BE-PSG-01-MAG10-AN026-XA0 | 2008-05-22 09:19 | 0
BE-PSG-01-MAG10-AN026-XA1 | 2008-05-22 09:19
BE-PSG-01-MAG10-AN031-XA0 | 2008-05-22 07:31 | 0
BE-PSG-01-MAG10-AN031-XA1 | 2008-05-22 07:31
BE-PSG-01-MAG10-AN032-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN032-XA1 | 2008-05-17 14:36
BE-PSG-01-MAG10-AN033-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN033-XA1 | 2008-05-17 14:35
BE-PSG-01-MAG10-AN034-XA0 | 2008-05-17 14:16 | 0
BE-PSG-01-MAG10-AN034-XA1 | 2008-05-17 14:16
BE-PSG-01-MAG10-AN035-XA0 | 2008-05-21 08:38 | 0
BE-PSG-01-MAG10-AN035-XA1 | 2008-05-21 08:38
BE-PSG-01-MAG10-AN036-XA0 | 2008-05-22 09:19 | 0
BE-PSG-01-MAG10-AN036-XA1 | 2008-05-22 09:19
BE-PSG-01-MAG10-AN041-XA0 | 2008-05-22 07:52 | 0
BE-PSG-01-MAG10-AN041-XA1 | 2008-05-22 07:52
BE-PSG-01-MAG10-AN042-XA0 | 2008-05-21 14:45 | 0
BE-PSG-01-MAG10-AN042-XA1 | 2008-05-21 14:45
BE-PSG-01-MAG10-AN043-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN043-XA1 | 2008-05-17 14:35
BE-PSG-01-MAG10-AN044-XA0 | 2008-05-17 14:35 | 0
BE-PSG-01-MAG10-AN044-XA1 | 2008-05-17 14:36
BE-PSG-01-MAG10-AN045-XA0 | 2008-05-21 09:30 | 0
BE-PSG-01-MAG10-AN045-XA1 | 2008-05-21 09:30
BE-PSG-01-MAG10-AN046-XA0 | 2008-05-22 10:45 | 0
BE-PSG-01-MAG10-AN046-XA1 | 2008-05-22 10:45
BE-PSG-01-MAG10-CT501-X3V | 2007-10-01 | 13.09
BE-PSG-01-MAG11-CT501-X1V | 2007-10-01 | 33.67
BE-PSG-01-MAG11-CT502-X1V | 2007-10-01 | 33.43
BE-PSG-01-MAG12-CT501-X1V | 2007-10-01 | 33.2
BE-PSG-01-MAG12-CT502-X1V | 2007-10-01 | 33.9
BE-PSG-01-MAG13-CT501-X1V | 2007-10-01 | 33.2
BE-PSG-01-MAG13-CT502-X1V | 2007-10-01 | 32.97
BE-PSG-01-MAG14-CT501-X1V | 2007-10-01 | 33.43
BE-PSG-01-MAG14-CT502-X1V | 2007-10-01 | 34.14
BE-PSG-01-MBM10-AP002-XA0 | 2008-05-17 15:58
BE-PSG-01-MBM10-AP002-XA1 | 2008-05-17 15:58 | 0
BE-PSG-01-MBM10-CE202B-XC7 | 2008-04-30 15:30 | 0
BE-PSG-01-MBM10-CF504-XC7 | 2007-10-01 | 0
BE-PSG-01-MBM10-CF505-X2V | 2008-04-30 11:12 | 0
BE-PSG-01-MBM10-CF506-X1V | 2008-04-30 11:12 | 0
BE-PSG-01-MBM10-CF507-X1V | 2008-04-30 11:12 | 0
BE-PSG-01-MBM10-CP503-XC7 | 2007-10-01 | 705.32
BE-PSG-01-MBM10-CP504-X1V | 2008-01-12 16:47 | 0.82034
BE-PSG-01-MBM10-CT502-X1V | 2008-05-06 16:46 | 23.7999
BE-PSG-01-MBM30-AA302L-X1V | 2008-04-30 11:12 | 0
BE-PSG-01-MBM30-AA302L-XH2 | 2008-05-17 15:58 | 0
BE-PSG-01-HAG25-CF601-X3V | 2007-10-01 | 27.54
BE-PSG-01-HAG40-CF601-X3V | 2007-10-01 | 32.41
BE-PSG-01-HAG80-CF601-X3V | 2007-10-01 | 249.65
BE-PSG-01-HAG00-EU901-X5V | 2007-10-01 | 319.9
BE-PSG-01-HAG00-EU903-X5V | 2008-04-26 11:01 | 1.0163
BE-PSG-01-LBA30-CP501-X3V | 2007-10-01 | 24.11
BE-PSG-01-LBA30-CT503-X3V | 2007-10-01 | 564.78
BE-PSG-01-LAE30-CF501-X1V | 2008-04-29 13:06 | 0
BE-PSG-01-MAN30-AA100X-X2H | 2014-04-28 14:04 | 0.98575
BE-PSG-01-CK00-EU902-X1V | 2007-10-01 | 105.99

## UNIT_CONVERSIONS
unit_from | unit_to | conversion_formula
F | C | (x - 32) * 5/9
K | C | x - 273.15
C | K | x + 273.15
Bar | mBar | x * 1000
mBar | Bar | x / 1000
Pa | Bar | x / 100000
Bar | Pa | x * 100000
Pa | mBar | x / 100
mBar | Pa | x * 100
mBar | MPa | x / 10000
MPa | mBar | x * 10000
Bar | MPa | x / 10
MPa | Bar | x * 10
Bar | kPa | x * 100
kPa | Bar | x / 100
mBar | kPa | x / 10
kPa | mBar | x * 10
Pa | MPa | x / 1000000
MPa | Pa | x * 1000000
Pa | kPa | x / 1000
kPa | Pa | x * 1000
Atm | Pa | x * 101325
Pa | Atm | x / 101325
Atm | Bar | x * 1.01325
Bar | Atm | x / 1.01325
kg_cm2 | Bar | x * 0.980665
Bar | kg_cm2 | x / 0.980665
Atm | mbar | x * 1013.25
mbar | Atm | x / 1013.25
kPa | mBar | x * 10
mBar | kPa | x / 10
Atm | kPa | x * 101.325
kPa | Atm | x / 101.325
MPa | Atm | x * 9.86923169
Atm | MPa | x * 0.101325
MPA | kPa | x * 1000
kPa | MPa | x / 1000
kg_s | ton_h | x * 3.6
ton_h | kg_s | x / 3.6
MW | W | x * 1000000
W | MW | x / 1000000
m | mm | x * 1000
mm | m | x / 1000
m | inch | x / 0.0254
inch | m | (1 / 0.0254) *x
m | ft | x / 0.3048
ft | m | (1 / 0.3048) *x
ft | inch | 12 * x
inch | ft | x / 12
m3_h | l_min | x * 16.666667
l_min | m3_h | x * 0.06
m3_h | m3_sec | x / 3600
m3_sec | m3_h | x * 3600
gal_min | m3_h | x * 0.227125
m3_h | gal_min | x * 4.402868
kg_h | lbm_h | x * 2.20462262
lbm_h | kg_h | x / 2.20462262
kJ | Btu | x * 0.94781712
Btu | kJ | x / 0.94781712
Bin | Perc | x * 100
Perc | Bin | floor(x / 100)
psi | Bar | x / 14.504
Bar | psi | x * 14.504
hPa | Atm | x/1013.25

## CBM_DASHBOARD
loc_code | Generic_Tag_Name | Tag_Description | Street | Module | Equipment | Type | Failure_Pattern | Threshold_Orange | Threshold_Red
BE-PSG | I_0101_MGE_0101HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0101HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0101HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_Highband | 1 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0101HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_LOOSNESS_HS_SHAFT | 1 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0101HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxHSshaft_Lowband | 1 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0101IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0101IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0101IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_Highband | 1 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0101IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_LOOSNESS_IM_SHAFT | 1 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0101IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxIMshaft_Lowband | 1 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0101LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0101LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 1 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0101LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_Highband | 1 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0101LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_LOOSNESS_LS_SHAFT | 1 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0101LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_Lowband | 1 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0101LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_GearboxLSshaft_UNBALANCE_LS_SHAFT | 1 | 1 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0101MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_Highband | 1 | 1 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0101MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_LOOSNESS_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0101MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_Lowband | 1 | 1 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0101MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0101MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motorcouplingside_UNBALANCE_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0101MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_Highband | 1 | 1 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0101MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_LOOSNESS_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0101MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_Lowband | 1 | 1 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0101MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0101MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0101MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_11_Motornoncouplingside_UNBALANCE_HS_SHAFT | 1 | 1 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MGE_0102HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0102HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0102HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_Highband | 1 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0102HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_LOOSNESS_HS_SHAFT | 1 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0102HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxHSshaft_Lowband | 1 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0102IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0102IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0102IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_Highband | 1 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0102IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_LOOSNESS_IM_SHAFT | 1 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0102IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxIMshaft_Lowband | 1 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0102LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0102LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 1 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0102LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_Highband | 1 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0102LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_LOOSNESS_LS_SHAFT | 1 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0102LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_Lowband | 1 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0102LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_GearboxLSshaft_UNBALANCE_LS_SHAFT | 1 | 2 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0102MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_Highband | 1 | 2 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0102MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_LOOSNESS_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0102MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_Lowband | 1 | 2 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0102MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0102MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motorcouplingside_UNBALANCE_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0102MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_Highband | 1 | 2 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0102MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_LOOSNESS_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0102MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_Lowband | 1 | 2 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0102MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0102MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0102MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_12_Motornoncouplingside_UNBALANCE_HS_SHAFT | 1 | 2 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MGE_0103HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0103HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0103HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_Highband | 1 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0103HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_LOOSNESS_HS_SHAFT | 1 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0103HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxHSshaft_Lowband | 1 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0103IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 1 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0103IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0103IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_Highband | 1 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0103IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_LOOSNESS_IM_SHAFT | 1 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0103IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxIMshaft_Lowband | 1 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0103LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 1 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0103LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 1 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 1 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0103LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_Highband | 1 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0103LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_LOOSNESS_LS_SHAFT | 1 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0103LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_Lowband | 1 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0103LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_GearboxLSshaft_UNBALANCE_LS_SHAFT | 1 | 3 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0103MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_Highband | 1 | 3 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0103MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_LOOSNESS_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0103MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_Lowband | 1 | 3 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0103MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0103MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motorcouplingside_UNBALANCE_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0103MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_Highband | 1 | 3 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0103MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_LOOSNESS_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0103MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_Lowband | 1 | 3 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0103MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0103MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 1 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0103MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_13_Motornoncouplingside_UNBALANCE_HS_SHAFT | 1 | 3 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MGE_0201HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0201HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0201HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_Highband | 2 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0201HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_LOOSNESS_HS_SHAFT | 2 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0201HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxHSshaft_Lowband | 2 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0201IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0201IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0201IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_Highband | 2 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0201IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_LOOSNESS_IM_SHAFT | 2 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0201IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxIMshaft_Lowband | 2 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0201LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 1 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0201LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 1 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 2 | 1 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0201LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_Highband | 2 | 1 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0201LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_LOOSNESS_LS_SHAFT | 2 | 1 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0201LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_Lowband | 2 | 1 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0201LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_GearboxLSshaft_UNBALANCE_LS_SHAFT | 2 | 1 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0201MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_Highband | 2 | 1 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0201MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_LOOSNESS_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0201MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_Lowband | 2 | 1 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0201MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0201MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motorcouplingside_UNBALANCE_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0201MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_Highband | 2 | 1 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0201MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_LOOSNESS_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0201MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_Lowband | 2 | 1 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0201MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0201MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 1 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0201MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_21_Motornoncouplingside_UNBALANCE_HS_SHAFT | 2 | 1 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MGE_0202HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0202HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0202HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_Highband | 2 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0202HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_LOOSNESS_HS_SHAFT | 2 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0202HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxHSshaft_Lowband | 2 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0202IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0202IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0202IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_Highband | 2 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0202IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_LOOSNESS_IM_SHAFT | 2 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0202IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxIMshaft_Lowband | 2 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0202LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 2 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0202LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 2 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 2 | 2 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0202LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_Highband | 2 | 2 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0202LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_LOOSNESS_LS_SHAFT | 2 | 2 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0202LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_Lowband | 2 | 2 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0202LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_GearboxLSshaft_UNBALANCE_LS_SHAFT | 2 | 2 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0202MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_Highband | 2 | 2 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0202MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_LOOSNESS_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0202MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_Lowband | 2 | 2 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0202MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0202MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motorcouplingside_UNBALANCE_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0202MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_Highband | 2 | 2 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0202MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_LOOSNESS_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0202MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_Lowband | 2 | 2 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0202MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0202MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 2 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0202MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_22_Motornoncouplingside_UNBALANCE_HS_SHAFT | 2 | 2 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MGE_0203HSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0203HSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203HSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203HSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE1_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE2_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_GEARBOX_BEARING_HS_SHAFT_TYPE3_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox high speed shaft | 1.2 | 1.8
BE-PSG | I_0101_MGE_0203HSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_Highband | 2 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox high speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0203HSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_LOOSNESS_HS_SHAFT | 2 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox high speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0203HSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxHSshaft_Lowband | 2 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox high speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0203IMGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_GMF | 2 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 1st set | 5.8 | 9
BE-PSG | I_0101_MGE_0203IMGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER1 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203IMGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_1ST_GEARSET_GMF_SER2 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 1 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203IMGSGMF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0203IMGSSER1_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203IMGSSER2_A_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203IMBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE1_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_GEARBOX_BEARING_IM_SHAFT_TYPE2_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox intermediate speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203IMHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_Highband | 2 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox intermediate speed shaft | 1 | 2
BE-PSG | I_0101_MGE_0203IMLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_LOOSNESS_IM_SHAFT | 2 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox intermediate speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0203IMLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxIMshaft_Lowband | 2 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox intermediate speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0203LSGSGMF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_GMF | 2 | 3 | Gearbox | A | Vibration change of gearbox gearmesh 2nd set | 5.8 | 9
BE-PSG | I_0101_MGE_0203LSGSSER1_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER1 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203LSGSSER2_A_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_2ND_GEARSET_GMF_SER2 | 2 | 3 | Gearbox | A | Vibration change indicating a damaged gear set 2 of the gearbox | 150 | 250
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE1_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE2_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_3_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE3_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_4_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE4_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_5_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE5_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFI_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFI | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (inner ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBPFO_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BPFO | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (outer ring) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRBSF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_BSF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (ball spin) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSBRFTF_A_X_6_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_GEARBOX_BEARING_LS_SHAFT_TYPE6_FTF | 2 | 3 | Gearbox | A | Vibration change indicating a bearing fault (cage) at the gearbox low speed shaft | 0.6 | 1.2
BE-PSG | I_0101_MGE_0203LSHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_Highband | 2 | 3 | Gearbox | V | Vibration change indicating high impacts at the gearbox low speed shaft | 0.5 | 1
BE-PSG | I_0101_MGE_0203LSLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_LOOSNESS_LS_SHAFT | 2 | 3 | Gearbox | A | Vibration change indicating loosness pattern at the gearbox low speed shaft | 5.8 | 9
BE-PSG | I_0101_MGE_0203LSLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_Lowband | 2 | 3 | Gearbox | V | Vibration change indicating a general high overall value at the gearbox low speed shaft | 7.1 | 11
BE-PSG | I_0101_MGE_0203LSUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_GearboxLSshaft_UNBALANCE_LS_SHAFT | 2 | 3 | Fan | A | Vibration change indicating a unbalance of the low speed fan shaft | 0.6 | 1.2
BE-PSG | I_0101_MOT_0203MCHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_Highband | 2 | 3 | Motor | V | Vibration change indicating high impacts at the motor shaft coupling side | 1 | 2
BE-PSG | I_0101_MOT_0203MCLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_LOOSNESS_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating loosness pattern at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0203MCLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_Lowband | 2 | 3 | Motor | V | Vibration change indicating a general high overall value at the motor shaft coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0203MCMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MISALIGNMENT_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating a misalignment at the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0203MCBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MCUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motorcouplingside_UNBALANCE_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating a unbalance of the motor shaft coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0203MNHB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_Highband | 2 | 3 | Motor | V | Vibration change indicating high impacts at the motor shaft non-coupling side | 1 | 2
BE-PSG | I_0101_MOT_0203MNLO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_LOOSNESS_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating loosness pattern at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0203MNLB_V_X_1_G | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_Lowband | 2 | 3 | Motor | V | Vibration change indicating a general high overall value at the motor shaft non-coupling side | 7.1 | 11
BE-PSG | I_0101_MOT_0203MNMA_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MISALIGNMENT_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating a misalignment at the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_MOT_0203MNBRBPFI_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFI | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRBPFO_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BPFO | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRBSF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_BSF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRFTF_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE1_FTF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRBPFI_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFI | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (inner ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRBPFO_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BPFO | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (outer ring) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRBSF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_BSF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (ball spin) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNBRFTF_A_X_2_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_MOTOR_BEARING_TYPE2_FTF | 2 | 3 | Motor | A | Vibration change indicating a bearing fault (cage) at the motor shaft non-coupling side | 1.2 | 1.8
BE-PSG | I_0101_MOT_0203MNUN_A_X_1_mm_s | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_23_Motornoncouplingside_UNBALANCE_HS_SHAFT | 2 | 3 | Motor | A | Vibration change indicating a unbalance of the motor shaft non-coupling side | 5.8 | 9
BE-PSG | I_0101_AMP_0101DBAMP_X_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP1_DeviceBattery | 1 | 1 | AMP | V | Sensor battery S1_AMP1 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0102DBAMP_X_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP1_DeviceBattery | 1 | 2 | AMP | V | Sensor battery S1_AMP1 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0102DBAMP_X_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP2_DeviceBattery | 1 | 2 | AMP | V | Sensor battery S1_AMP2 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0103DBAMP_X_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP2_DeviceBattery | 1 | 3 | AMP | V | Sensor battery S1_AMP2 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0103DBAMP_X_X_3_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP3_DeviceBattery | 1 | 3 | AMP | V | Sensor battery S1_AMP3 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0101DBAMP_X_X_3_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP3_DeviceBattery | 1 | 1 | AMP | V | Sensor battery S1_AMP3 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0102DBAMP_X_X_4_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP4_DeviceBattery | 1 | 2 | AMP | V | Sensor battery S1_AMP4 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0103DBAMP_X_X_4_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S1_AMP4_DeviceBattery | 1 | 3 | AMP | V | Sensor battery S1_AMP4 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0201DBAMP_X_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP1_DeviceBattery | 2 | 1 | AMP | V | Sensor battery S2_AMP1 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0202DBAMP_X_X_1_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP1_DeviceBattery | 2 | 2 | AMP | V | Sensor battery S2_AMP1 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0202DBAMP_X_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP2_DeviceBattery | 2 | 2 | AMP | V | Sensor battery S2_AMP2 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0203DBAMP_X_X_2_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP2_DeviceBattery | 2 | 3 | AMP | V | Sensor battery S2_AMP2 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0203DBAMP_X_X_3_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP3_DeviceBattery | 2 | 3 | AMP | V | Sensor battery S2_AMP3 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0201DBAMP_X_X_3_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP3_DeviceBattery | 2 | 1 | AMP | V | Sensor battery S2_AMP3 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0202DBAMP_X_X_4_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP4_DeviceBattery | 2 | 2 | AMP | V | Sensor battery S2_AMP4 level is below [%] | 7 | 6
BE-PSG | I_0101_AMP_0203DBAMP_X_X_4_ | SPX_DC_ENGIE_SAINTGHISLAIN_ACC_S2_AMP4_DeviceBattery | 2 | 3 | AMP | V | Sensor battery S2_AMP4 level is below [%] | 7 | 6

## DCS_DASHBOARD
loc_code | msg_id | msg_code | Group | Failure_Pattern | Threshold_level | Priority | Description
BE-PSG | m09 | CL_SUBCOOLING_#_MSG | STREET_SUBCOOLING | Subcooling at condensate line higher than expected | Yellow | 1 | Street #
BE-PSG | m10 | CL_SUBCOOLING_#_MSG | STREET_SUBCOOLING | Subcooling at condensate line too high | Red | 1 | Street #
BE-PSG | m11 | ATO_SUBCOOLING_#_MSG | STREET_SUBCOOLING | Subcooling at air take off line higher than expected | Yellow | 2 | Street #
BE-PSG | m12 | ATO_SUBCOOLING_#_MSG | STREET_SUBCOOLING | Subcooling at air take off too high | Red | 2 | Street #
BE-PSG | m13 | SUBCOOLING_TANK_MSG | CONDENSATE_TANK | Subcooling in condensate return line higher than expected | Yellow | 1 | Tank /subcooling
BE-PSG | m14 | SUBCOOLING_TANK_MSG | CONDENSATE_TANK | Subcooling in condensate return line too high | Red | 1 | Tank /subcooling
BE-PSG | m15 | O2_TANK_MSG | CONDENSATE_TANK | O2 content at tank outlet higher than expected | Yellow | 2 | Tank/O2
BE-PSG | m16 | O2_TANK_MSG | CONDENSATE_TANK | O2 content at tank outlet too high | Red | 2 | Tank/O2
BE-PSG | m17 | AIR_TANK_OFF_MSG | VACCUM_SYSTEM | Subcooling at air take off line higher than expected | Yellow | 1 | Vaccum syst
BE-PSG | m18 | AIR_TANK_OFF_MSG | VACCUM_SYSTEM | Subcooling at air take off too high | Red | 1 | Vaccum syst
BE-PSG | m19 | MOTIVE_PRESSURE_MSG | VACCUM_SYSTEM | Motive pressure out of operational range | Red | 2 | Vaccum syst
BE-PSG | m20 | MOTIVE_TEMPERATURE_MSG | VACCUM_SYSTEM | Motive temperature out of operational range | Red | 3 | Vaccum syst
BE-PSG | m21 | COOLING_TEMPERATURE_MSG | VACCUM_SYSTEM | Cooling temperature out of operational range | Red | 4 | Vaccum syst
BE-PSG | m22 | SUBCOOLING_MSG | SUBCOOLING | Subcooling at condensate tank outlet higher than usual | Yellow |  | Subcooling
BE-PSG | m23 | SUBCOOLING_MSG | SUBCOOLING | Subcooling at condensate tank outlet too high | Red |  | Subcooling
BE-PSG | m24 | CONDENSATE_PUMP_MSG | CONDENSATE_PUMP | Moderate change of vibration detected on condensate extraction pump | Yellow |  | Vibration level unusual on condensate extraction pump
BE-PSG | m25 | CONDENSATE_PUMP_MSG | CONDENSATE_PUMP | High change of vibration detected on condensate extraction pump | Red |  | Vibration level abnormal on condensate extraction pump
BE-PSG | m26 | DRAIN_PUMP_MSG | DRAIN_PUMP | Moderate change of vibration detected on drain pump | Yellow |  | Vibration level unusual on Drain pump
BE-PSG | m27 | DRAIN_PUMP_MSG | DRAIN_PUMP | High change of vibration detected on drain pump | Red |  | Vibration level abnormal on Drain pump

## DASHBOARD_ENVIRONMENTS
active | loc_code | env_code | web_url | api_url | web_user | web_pw | db_server | db_port | db_name | db_schema | db_user | db_password
N | BE-PSG | TST | tst.rpm.acc-360.com | https://tst-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-tst-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_tst_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | BE-PSG | UAT | uat.rpm.acc-360.com | https://uat-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-uat-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_uat_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
Y | BE-PSG | PRD | rpm.acc-360.com | https://api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-prd-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_prd_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Demo | TST | tst.rpm.acc-360.com | https://tst-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-tst-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_tst_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Demo | UAT | uat.rpm.acc-360.com | https://uat-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-uat-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_uat_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Demo | PRD | rpm.acc-360.com | https://api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-prd-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_prd_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Snap | TST | tst.rpm.acc-360.com | https://tst-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-tst-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_tst_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Snap | UAT | uat.rpm.acc-360.com | https://uat-api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-uat-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_uat_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818
N | ACC_Snap | PRD | rpm.acc-360.com | https://api.rpm.acc-360.com | sas | {SAS004}05A0A0364DA6C92BB9C2EA2919CB2801F4642A3F1A85B8D92494F125E0BCE94737F225BE6A5816120CBC81C3DADEAB5B83D72578271B70C71566092B69A6ED5ED432E5A91985C78DF549ECDE835CBA2CB14607C502F2A6568048103D73CEF22353A80E007D60F630FED00F9E0190944CAF481D4D2541BA7B | rds-spx-prd-01.clbzndnyqu7a.eu-west-1.rds.amazonaws.com | 3306 | rds_spx_prd_01 | default | dbmaster | {SAS004}95079700A68C0262DC1D63C20B1C6CB0A7A82C8E089BDEA720875B9C82A493FAFF461E21375F4818

## ABT_THRESHOLD
loc_code | Tag_name | Unit | Active | Threshold_min | Threshold_max | Failure_Pattern | Description
BE-PSG | ste_flow |  | Y | 200 | 370 | Steam flow not in threshold limit | validate when plan in operation
BE-PSG | power_plant_output |  | Y | 160 | 360 | Power plant output not in threshold limit | validate when plan in operation
BE-PSG | air_temp |  | Y | -8 | 38 | Air temperature not in threshold limit
BE-PSG | air_press |  | Y | 1000 | 1050 | Air pressure not in threshold limit
BE-PSG | ste_press |  | Y | 0.05 | 0.16 | Steam pressure not in threshold limit | validate when plan in operation
BE-PSG | ste_temp |  | Y | 30 | 56 | Steam temperature not in threshold limit | validate when plan in operation
BE-PSG | wind_speed |  | N
BE-PSG | cdt_temp |  | N
BE-PSG | con_temp_01L |  | N
BE-PSG | con_temp_01R |  | N
BE-PSG | con_temp_02L |  | N
BE-PSG | con_temp_02R |  | N
BE-PSG | con_temp_03L |  | N
BE-PSG | con_temp_03R |  | N
BE-PSG | con_temp_04L |  | N
BE-PSG | con_temp_04R |  | N
BE-PSG | sec_temp_01L |  | N
BE-PSG | sec_temp_01R |  | N
BE-PSG | sec_temp_02L |  | N
BE-PSG | sec_temp_02R |  | N
BE-PSG | sec_temp_03L |  | N
BE-PSG | sec_temp_03R |  | N
BE-PSG | sec_temp_04L |  | N
BE-PSG | sec_temp_04R |  | N
BE-PSG | st_output_orig |  | N
BE-PSG | ste_dryness |  | N
BE-PSG | ste_flow_dry_percent |  | N
BE-PSG | heat_load_current |  | N
BE-PSG | bp_current |  | N
BE-PSG | acc_itd |  | N
BE-PSG | fan_power_current |  | N
BE-PSG | st_output_current |  | N
BE-PSG | min_bp |  | N
BE-PSG | bp_theoretical |  | N
BE-PSG | delta_bp |  | N
BE-PSG | delta_bp_perc |  | N
BE-PSG | ste_flow_predicted |  | N
BE-PSG | ste_flow_pred_unfilt |  | N
BE-PSG | capa_current |  | N
BE-PSG | con_subcooling_01L |  | N
BE-PSG | con_subcooling_01R |  | N
BE-PSG | con_subcooling_02L |  | N
BE-PSG | con_subcooling_02R |  | N
BE-PSG | con_subcooling_03L |  | N
BE-PSG | con_subcooling_03R |  | N
BE-PSG | con_subcooling_04L |  | N
BE-PSG | con_subcooling_04R |  | N
BE-PSG | con_subcooling_avg |  | N
BE-PSG | sec_subcooling_01L |  | N
BE-PSG | sec_subcooling_01R |  | N
BE-PSG | sec_subcooling_02L |  | N
BE-PSG | sec_subcooling_02R |  | N
BE-PSG | sec_subcooling_03L |  | N
BE-PSG | sec_subcooling_03R |  | N
BE-PSG | sec_subcooling_04L |  | N
BE-PSG | sec_subcooling_04R |  | N
BE-PSG | sec_subcooling_avg |  | N
BE-PSG | cdt_subcooling |  | N
BE-PSG | subcooling_current |  | N